# FINDINGS OF FACT

After review of the air emission license renewal and amendment application, staff investigation reports, and other documents in the applicant’s file in the Bureau of Air Quality, pursuant to 38 Maine Revised Statutes (M.R.S.) § 344 and § 590, the Maine Department of Environmental Protection (Department) finds the following facts:

## REGISTRATION

### Introduction

City of Bangor, Bangor International Airport (BGR) has applied to renew their Air Emission License for the operation of emission sources associated with their air travel facility.

BGR has requested an amendment to their license as follows:

- Add a new 2,000 ekW emergency generator, Generator IAB-4, to be located adjacent to the parking lot north of the International terminal;

- Remove the previously licensed Generator 99-1 (manufactured in 2002) and replace it with a new unit, also designated Generator 99-1, manufactured in 2020 and installed July 1, 2021;

- Remove the previously licensed Boiler 253-1 (manufactured in 1998) and replace it with a new unit designated 253-2 manufactured in 2025 and installed in 2025;

- Remove Generator 461-2;

- Remove the Spray Paint Booth from their license;

- Remove Jet A fuel from all boilers and Snow Melter #1, except Boilers 461-1, 462-1, 463-1, and 464-1; and

- Add a heat input/fuel limit specifically for Boilers 461-1, 462-1, 463-1, and 464-1.

Additionally, the SO2 and visible emissions requirements will be updated to reflect new standards based on current rules.

The equipment addressed in this license is located at 287 Godfrey Boulevard, Bangor, Maine.

### Emission Equipment

The following equipment is addressed in this air emission license:

Fuel Burning Equipment

| ### Equipment | Max. Capacity (MMBtu/hr) | Maximum Firing Rate | Fuel Type | Date of Manuf. | ### Date of Install. | ### Stack # |
| --- | --- | --- | --- | --- | --- | --- |
| Boiler IAB-1 | 4.18 | 29.9 gal/hr | Distillate Fuel | 1974 | ### 1974 | ### IAB-1 |
|  |  | 4,180 scf/hr | Natural Gas |  |  |  |
| Boiler IAB-2 | 4.18 | 29.9 gal/hr | Distillate Fuel | 1992 | ### 1992 | ### IAB-2 |
|  |  | 4,180 scf/hr | Natural Gas |  |  |  |
| Boiler DAB-1A | 6.12 | 43.7 gal/hr | Distillate Fuel | 2009 | ### 2009 | ### DAB-1A |
|  |  | 6,124 scf/hr | Natural Gas |  |  |  |
| Boiler 461-1 | 6.30 | 45 gal/hr | Distillate Fuel or Jet A Fuel | 1959 | ### 1959 | ### 461-1 |
|  |  | 6,300 scf/hr | Natural Gas |  |  |  |
| Boiler 462-1 | 6.12 | 43.7 gal/hr | Distillate Fuel or Jet A Fuel | 2002 | ### 2002 | ### 462-1 |
|  |  | 6,124 scf/hr | Natural Gas |  |  |  |
| Boiler 463-1 | 6.12 | 43.7 gal/hr | Distillate Fuel or Jet A Fuel | 2003 | ### 2003 | ### 463-1 |
|  |  | 6,124 scf/hr | Natural Gas |  |  |  |
| Boiler 464-1 | 6.28 | 44.9 gal/hr | Distillate Fuel or Jet A Fuel | 2001 | ### 2001 | ### 464-1 |
|  |  | 6,280 scf/hr | Natural Gas |  |  |  |
| Boiler 457-1 | 2.77 | 19.8 gal/hr | Distillate Fuel | 1997 | ### 1997 | ### 457-1 |
|  |  | 2,770 scf/hr | Natural Gas |  |  |  |
| Boiler 268-1 | 2.77 | 19.8 gal/hr | Distillate Fuel | 1998 | ### 1998 | ### 268-1 |
|  |  | 2,770 scf/hr | Natural Gas |  |  |  |
| Boiler 271-1 | 1.50 | 10.7 gal/hr | Distillate Fuel | 1979 | ### 1979 | ### 271-1 |
|  |  | 1,500 scf/hr | Natural Gas |  |  |  |
| Boiler 253-1 a | 1.50 | 10.7 gal/hr | Distillate Fuel | 1998 | ### 1998 | ### 253-1 |
|  |  | 1,500 scf/hr | Natural Gas |  |  |  |
| Boiler 253-2 b | 1.68 | 1,680 scf/hr | Natural Gas | 2025 | ### 2025 | ### 253-1 |
| Boiler 96-1 | 1.50 | 10.7 gal/hr | Distillate Fuel | 1989 | ### 1989 | ### 96-1 |
|  |  | 1,500 scf/hr | Natural Gas |  |  |  |
| Boiler 100-1 | 2.77 | 19.8 gal/hr | Distillate Fuel | 1987 | ### 1987 | ### 100-1 |
|  |  | 2,770 scf/hr | Natural Gas |  |  |  |
| Boiler 100-2 | 2.80 | 20 gal/hr | Distillate Fuel | 1998 | ### 1998 | ### 100-2 |
|  |  | 2,800 scf/hr | Natural Gas |  |  |  |
| Boiler 269-1 | 1.58 | 11.4 gal/hr | Distillate Fuel | 1998 | ### 1998 | ### 269-1 |
|  |  | 1,580 scf/hr | Natural Gas |  |  |  |
| Snow Melter #1 | 8.96 | 64 gal/hr | Distillate Fuel | - | ### - | ### Fugitive |

a Removed from license

b New to license

Generators

| ### Equipment | Engine Serial Number | Max. Input Capacity (MMBtu/hr) | Rated Output Capacity | Fuel Type | Firing Rate (gal/hr) | Date of Manuf. | ### Stack |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator DAB-3 | FST 01198 | 5.9 | 600 kW | Distillate Fuel | 42.7 | 2015 | DAB-3 |
| Generator IAB-3 | 79518957 | 4.7 | 600 kW | Distillate Fuel | 34.7 | 2012 | IAB-3 |
| Generator 461-2 a | U976262G | 0.75 | 80 kW | Distillate Fuel | 5.4 | 2001 | 461-2 |
| Generator 99-1 b | PW301174 | 3.75 | 385 kW | Distillate Fuel | 27 | 2020 | 99-1 |
| Generator TF-1 | RG6076A202748 | 1.68 | 170 kW | Distillate Fuel | 12.1 | 1999 | TF-1 |
| BLDG 600-1 Generator | AD20405SPF | 1.4 | 145 kW | Distillate Fuel | 10.1 | 1992 | 600-2 |
| Generator IAB-4 c | S16R-72PTAW2-1 | 21.24 | 2,000 kW | Distillate Fuel | 155 | 2025 | IAB-4 |

a Removed from license

b Generator 99-1 was replaced with a new model on July 1, 2021

c New to license

Volatile Organic Liquid Storage Tanks

| ### Tank Name | Tank Type | Capacity (gallons) | Materials Stored | Date of Manuf. | ### Control Device |
| --- | --- | --- | --- | --- | --- |
| T-1 | Floating Geodome | 630,000 | Jet A Fuel | 1955 (Upgraded in 2000) | None |
| T-2 | Fixed Cone | 2,000,000 | Jet A Fuel | 1955 (Upgraded in 1998) | None |
| T-3 | Fixed Cone | 630,000 | Jet A Fuel | 1955 (Upgraded in 2001) | None |
| T-4 | Horizontal Welded | 12,000 | Low Lead Aviation Gas | 1991 | Vapor Recovery |
| T-5 | Horizontal Welded | 12,000 | Gasoline | 1991 | Vapor Recovery |
| T-6 a | Horizontal Welded | 10,000 | Biodiesel | 2008 | - |

a T-6 is an insignificant activity per 06-096 C.M.R. ch. 115, Appendix B Section B(7), and therefore is not addressed further in this air license.

In addition to T-6, BGR operates four 10,000 gallon, underground storage tanks located near Boilers 461-1, 462-1, 463-1, and 464-1, specifically for the storage of Jet A fuel to be combusted in those boilers. These tanks are insignificant activities per 06-096 C.M.R. ch.115, Appendix B Section B(7), and therefore are not addressed further in this air license.

BGR no longer operates the Paint Spray Booth. It was removed from service in 2017 and is hereby removed from their air emission license.

### Definitions

Distillate Fuel means the following:

- Fuel oil that complies with the specifications for fuel oil numbers 1 or 2, as defined by the American Society for Testing and Materials (ASTM) in ASTM D396;

- Diesel fuel oil numbers 1 or 2, as defined in ASTM D975;

- Kerosene, as defined in ASTM D3699;

- Biodiesel, as defined in ASTM D6751; or

- Biodiesel blends, as defined in ASTM D7467.

Jet A Fuel means fuel oil that complies with the specifications for aviation turbine fuels, as defined by ASTM D1655-22.

Records or Logs mean either hardcopy or electronic records.

### Application Classification

All rules, regulations, or statutes referenced in this air emission license refer to the amended version in effect as of the date this license was issued.

BGR has applied to renew currently licensed emission units as well as modify their license as addressed in Section I(A) above.

The modification of a minor source is considered a major or minor modification based on whether or not expected emission increases exceed the “Significant Emissions” levels as defined in the Department’s Definitions Regulation, 06-096 Code of Maine Rules (C.M.R.) ch. 100. The emission increases are determined by subtracting the current licensed annual emissions preceding the modification from the maximum future licensed annual emissions, as follows:

| Pollutant | Current License (tpy) | Future License (tpy) | Net Change (tpy) | Significant Emissions Levels |
| --- | --- | --- | --- | --- |
| PM | 6.9 | 6.2 | -0.7 | 100 |
| PM10 | 6.9 | 6.2 | -0.7 | 100 |
| PM2.5 | - | 6.2 | - | 100 |
| SO2 | 25.7 | 14.8 | -10.9 1 | 100 |
| NOx | 19.8 | 13.7 | -6.1 1 | 100 |
| CO | 7.1 | 5.7 | -1.4 | 100 |
| VOC | 12.8 | 2.9 | -9.9 2 | 100 |

- SO2 and NOx emissions greatly decreased due to lower maximum distillate fuel sulfur content included in state statute since the previous license renewal and NOx corrections applied to the snow melter and emergency generators.

- VOC emissions were greatly reduced due to the removal of the Paint Spray Booth.

Therefore, this license is considered to be both a renewal and a minor modification and has been processed through Major and Minor Source Air Emission License Regulations, 06-096 Code of Maine Rules C.M.R. ch. 115.

### Facility Classification

With the annual fuel use limit on the existing boilers and the operating hours restriction on the emergency generators and the snow melter, the facility is licensed as follows:

- As a synthetic minor source of air emissions for criteria pollutants, because BGR is subject to license restrictions that keep facility emissions below major source thresholds for NOx and CO; and

- As an area source of hazardous air pollutants (HAP), because the licensed emissions are below the major source thresholds for HAP.

## BEST PRACTICAL TREATMENT (BPT)

### Introduction

In order to receive a license, the applicant must control emissions from each unit to a level considered by the Department to represent Best Practical Treatment (BPT), as defined in Definitions Regulation, 06-096 C.M.R. ch. 100. Separate control requirement categories exist for new and existing equipment.

BPT for new sources and modifications requires a demonstration that emissions are receiving Best Available Control Technology (BACT), as defined in Definitions Regulation, 06-096 C.M.R. ch. 100. BACT is a top-down approach to selecting air emission controls considering economic, environmental, and energy impacts.

BPT for existing emissions equipment means that method which controls or reduces emissions to the lowest possible level considering:

- the existing state of technology;

- the effectiveness of available alternatives for reducing emissions from the source being considered; and

- the economic feasibility for the type of establishment involved.

### Boilers

BGR operates 15 boilers (listed below) to provide heat and hot water to various airport buildings. All of the boilers are maintained by a licensed boiler technician and have regular boiler tune-ups in accordance with state and federal requirements.

| Equipment | Licensed Fuels | Max. Capacity (MMBtu/hr) | Date of Manuf. & Install. |
| --- | --- | --- | --- |
| Boiler IAB-1 | Distillate Fuel and Natural Gas | 4.18 | 1974 |
| Boiler IAB-2 | Distillate Fuel and Natural Gas | 4.18 | 1992 |
| Boiler DAB-1A | Distillate Fuel and Natural Gas | 6.12 | 2009 |
| Boiler 461-1 | Distillate and Jet A Fuels and Natural Gas | 6.3 | 1959 |
| Boiler 462-1 | Distillate and Jet A Fuels and Natural Gas | 6.12 | 2002 |
| Boiler 463-1 | Distillate and Jet A Fuels and Natural Gas | 6.12 | 2003 |
| Boiler 464-1 | Distillate and Jet A Fuels and Natural Gas | 6.28 | 2001 |
| Boiler 457-1 | Distillate Fuel and Natural Gas | 2.77 | 1997 |
| Boiler 268-1 | Distillate Fuel and Natural Gas | 2.77 | 1998 |
| Boiler 271-1 | Distillate Fuel and Natural Gas | 1.50 | 1979 |
| Boiler 253-2 | Natural Gas | 1.68 | 2025 |
| Boiler 96-1 | Distillate Fuel and Natural Gas | 1.50 | 1989 |
| Boiler 100-1 | Distillate Fuel and Natural Gas | 2.77 | 1987 |
| Boiler 100-2 | Distillate Fuel and Natural Gas | 2.80 | 1998 |
| Boiler 269-1 | Distillate Fuel and Natural Gas | 1.58 | 1998 |

With limited exceptions, no person shall import, distribute, or offer for sale any distillate fuel with a sulfur content greater than 0.0015% by weight (15 ppm) pursuant to 38 M.R.S. § 603-A(2)(A)(3). Therefore, the distillate fuel purchased or otherwise obtained for use in any of the licensed boilers shall not exceed 0.0015% by weight (15 ppm).

##### BACT Findings

The following is a BACT analysis for control of emissions from Boiler 253-2.

- Particulate Matter (PM, PM10, PM2.5)

BGR has proposed to burn only natural gas in the boiler to minimize PM emissions.

BACT for PM/PM10/PM2.5 emissions from Boiler 253-2 is the combustion of natural gas and the emission limits listed in the tables below.

- Sulfur Dioxide (SO2)

BGR has proposed to fire only natural gas, which has inherently low sulfur content.

BACT for SO2 emissions from Boiler 253-2 is the use of natural gas and the emission limits listed in the tables below.

- Nitrogen Oxides (NOx), Carbon Monoxide (CO), and Volatile Organic Compounds (VOC)

BGR looked into the use of add-on controls such as SCR, SNCR, or oxidation catalysts. Due to the small size of the unit and anticipated NOx, CO, and VOC emissions, additional controls were economically infeasible.

BACT for NOx, CO, and VOC is good combustion practices and the emission limits listed in the tables below.

- Emission Limits

The BACT emission limits for Boiler 253-2 were based on the following:

Natural Gas

| PM/PM10/PM2.5 | – | 0.05 lb/MMBtu, 06-096 C.M.R. ch. 115, BACT |
| --- | --- | --- |
| SO2 | – | 0.6 lb/MMscf based on AP-42 Table 1.4-2 dated 7/98 |
| NOx | – | 100 lb/MMscf based on AP-42 Table 1.4-1 dated 7/98 |
| CO | – | 84 lb/MMscf based on AP-42 Table 1.4-1 dated 7/98 |
| VOC | – | 5.5 lb/MMscf based on AP-42 Table 1.4-2 dated 7/98 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

##### BPT Findings

The BPT emission limits for the boilers in the table above (other than Boiler 253-2) were based on the following:

Distillate Fuel/Jet A Fuel

| PM/PM10/PM2.5 | – | 0.12 lb/MMBtu, 06-096 C.M.R. ch. 103 (for those units with heat inputs of 3.0 MMBtu/hr or greater); 0.12 lb/MMBtu, 06-096 C.M.R. ch. 115, BPT (for those units with heat inputs less than 3.0 MMBtu/hr) |
| --- | --- | --- |
| SO2 | – | based on firing fuel with a maximum sulfur content of 0.0015% by weight for distillate fuel and 1.5% by weight for Jet A fuel |
| NOx | – | 20 lb/1,000 gal based on AP-42 Table 1.3-1 dated 5/10 |
| CO | – | 5 lb/1,000 gal based on AP-42 Table 1.3-1 dated 5/10 |
| VOC | – | 0.34 lb/1,000 gal based on AP-42 Table 1.3-3 dated 5/10 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

Natural Gas

| PM/PM10/PM2.5 | – | 0.05 lb/MMBtu, 06-096 C.M.R. ch. 115, BPT |
| --- | --- | --- |
| SO2 | – | 0.6 lb/MMscf based on AP-42 Table 1.4-2 dated 7/98 |
| NOx | – | 100 lb/MMscf based on AP-42 Table 1.4-1 dated 7/98 |
| CO | – | 84 lb/MMscf based on AP-42 Table 1.4-1 dated 7/98 |
| VOC | – | 5.5 lb/MMscf based on AP-42 Table 1.4-2 dated 7/98 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BPT emission limits for the boilers identified below are the following:

| Unit | Fuel Type | Pollutant | lb/MMBtu |
| --- | --- | --- | --- |
| Boiler IAB-1 | Distillate Fuel | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler IAB-2 | Distillate Fuel | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler DAB-1A | Distillate Fuel | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 461-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 462-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 463-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 464-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |

The BPT emission limits for the boilers identified below are based on firing the fuel with the highest emission factor.

| Emission Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler IAB-1 | 0.50 | 0.50 | 0.50 | 0.01 | 0.60 | 0.34 | 0.02 |
| Boiler IAB-2 | 0.50 | 0.50 | 0.50 | 0.01 | 0.60 | 0.34 | 0.02 |
| Boiler DAB-1A | 0.73 | 0.73 | 0.73 | 0.01 | 0.87 | 0.50 | 0.03 |
| Boiler 461-1 | 0.76 | 0.76 | 0.76 | 9.52 | 0.90 | 0.51 | 0.03 |
| Boiler 462-1 | 0.73 | 0.73 | 0.73 | 9.25 | 0.87 | 0.50 | 0.03 |
| Boiler 463-1 | 0.73 | 0.73 | 0.73 | 9.25 | 0.87 | 0.50 | 0.03 |
| Boiler 464-1 | 0.75 | 0.75 | 0.75 | 9.49 | 0.90 | 0.51 | 0.03 |
| Boiler 457-1 | 0.33 | 0.33 | 0.33 | - | 0.40 | 0.23 | 0.01 |
| Boiler 268-1 | 0.33 | 0.33 | 0.33 | - | 0.40 | 0.23 | 0.01 |
| Boiler 271-1 | 0.18 | 0.18 | 0.18 | - | 0.21 | 0.12 | 0.01 |
| Boiler 253-2 | 0.08 | 0.08 | 0.08 | - | 0.16 | 0.14 | 0.01 |
| Boiler 96-1 | 0.18 | 0.18 | 0.18 | - | 0.21 | 0.12 | 0.01 |
| Boiler 100-1 | 0.33 | 0.33 | 0.33 | - | 0.40 | 0.23 | 0.01 |
| Boiler 100-2 | 0.34 | 0.34 | 0.34 | - | 0.40 | 0.23 | 0.01 |
| Boiler 269-1 | 0.19 | 0.19 | 0.19 | - | 0.23 | 0.13 | 0.01 |

BGR shall be limited to no more than 98,000 MMBtu/year of heat input for all boilers addressed in this license. BGR shall maintain records of the total of distillate fuel, Jet A fuel, and natural gas fired in these boilers, and the MMBtu/year shall be calculated using the following factors:

Distillate fuel:	0.14 MMBtu/gallon

Jet A fuel:	0.14 MMBtu/gallon

Natural Gas:	0.00103 MMBtu/scf

This limit applies to licensed emission units only and excludes insignificant activities.

As part of this total heat input limit, BGR shall be limited to firing no more than 19,500 MMBtu/year in Boilers 461-1, 462-1, 463-1, and/or 464-1 combined, the equivalent of 139,286 gallons of Jet A fuel.

##### Visible Emissions

When firing distillate fuel or Jet A fuel, visible emissions from each boiler shall not exceed 20% opacity on a six-minute block average basis.

When firing natural gas, visible emissions from each boiler shall not exceed 10% opacity on a six-minute block average basis.

##### Periodic Monitoring

Periodic monitoring for the boilers shall include recordkeeping to document fuel use both on a monthly and calendar year total basis. Documentation shall include the type of fuel used and sulfur content of the fuel.

##### New Source Performance Standards (NSPS): 40 C.F.R. Part 60, Subpart Dc

Due to their sizes, none of the boilers addressed in this section are subject to Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units, 40 C.F.R. Part 60, Subpart Dc for units greater than 10 MMBtu/hr manufactured after June 9, 1989. [40 C.F.R. § 60.40c]

##### National Emission Standards for Hazardous Air Pollutants (NESHAP): 40 C.F.R. Part 63, Subpart JJJJJJ

Boilers IAB-1, IAB-2, DAB-1A, 461-1, 462-1, 463-1, 464-1, 457-1, 268-1, 271-1, 253-2, 100-1, and 100-2 are subject to the National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources, 40 C.F.R. Part 63, Subpart JJJJJJ. These units are considered existing oil boilers rated less than 10 MMBtu/hr. Units not subject to the requirements of this subpart include hot water heaters, as defined in this subpart and including hot water boilers (i.e., those not generating steam) combusting gaseous, liquid, or biomass fuel and with a heat input capacity of less than 1.6 million Btu per hour. [40 C.F.R. § 63.11195] Although Boiler 271-1 is rated at less than 1.6 MMBtu/hr, it produces steam and therefore is not considered exempt in the “hot water heater” category under Subpart JJJJJJ. Boilers 96-1 and 269-1 do not generate steam and therefore are exempt from Subpart JJJJJJ. [40 C.F.R. §§ 63.11193 and 63.11195]

Applicable federal 40 C.F.R. Part 63, Subpart JJJJJJ requirements include the following. Additional rule information can be found on the following website: https://www.epa.gov/stationary-sources-air-pollution/compliance-industrial-commercial-and-institutional-area-source.

- Compliance Dates, Notifications, and Work Practice Requirements

- Boiler Tune-Up Program

- A boiler tune-up program shall be implemented. [40 C.F.R. § 63.11223]

- Tune-ups shall be conducted at a frequency specified by the rule and based on the size, age, and operations of the boiler. See chart below:

| Boiler Category | Tune-Up Frequency |
| --- | --- |
| Existing Oil fired boilers that are not designated as "Boilers with Less Frequent Tune-up Requirements" (Boiler DAB-1A, Boiler 461-1, Boiler 462-1, Boiler 463-1, Boiler 464-1) | Every 2 years |
| Oil fired boilers with a heat input capacity of ≤ 5MMBtu/hr (Boiler IAB-1, Boiler IAB-2, Boiler 457-1, Boiler 268-1, Boiler 271-1, Boiler 253-2, Boiler 100-1, Boiler 100-2) | Every 5 years |

[40 C.F.R. § 63.11223(a) and Table 2]

- The boiler tune-up program, conducted to demonstrate continuous compliance, shall be performed as specified below:

- As applicable, inspect the burner, and clean or replace any component of the burner as necessary. Delay of the burner inspection until the next scheduled shutdown is permitted, not to exceed 36 months from the previous inspection. Delay of the burner inspection until the next scheduled shutdown is permitted for up to 72 months from the previous inspection for oil fired boilers less than or equal to 5 MMBtu/hour. [40 C.F.R. § 63.11223(b)(1)]

- Inspect the flame pattern, as applicable, and adjust the burner as necessary to optimize the flame pattern, consistent with the manufacturer’s specifications. [40 C.F.R. § 63.11223(b)(2)]

- Inspect the system controlling the air-to-fuel ratio, as applicable, and ensure it is correctly calibrated and functioning properly. Delay of the inspection until the next scheduled shutdown is permitted, not to exceed 36 months from the previous inspection. Delay of the inspection until the next scheduled shutdown is permitted for up to 72 months from the previous inspection for oil fired boilers less than or equal to 5 MMBtu/hour. [40 C.F.R. § 63.11223(b)(3)]

- Optimize total emissions of CO, consistent with manufacturer’s specifications. [40 C.F.R. § 63.11223(b)(4)]

- Measure the concentration in the effluent stream of CO in parts per million by volume (ppmv), and oxygen in volume percent, before and after adjustments are made (measurements may be either on a dry or wet basis, as long as it is the same basis before and after the adjustments are made). Measurements may be taken using a portable CO analyzer. [40 C.F.R. § 63.11223(b)(5)]

- If a unit is not operating on the required date for a tune-up, the tune-up must be conducted within 30 days of start-up.

[40 C.F.R. § 63.11223(b)(7)]

- Tune-Up Report: A tune-up report shall be maintained onsite and, submitted to the Department and/or EPA upon request. The report shall contain the following information:

- The concentration of CO in the effluent stream (ppmv) and oxygen (volume percent) measured at high fire or typical operating load both before and after the boiler tune-up;

- A description of any corrective actions taken as part of the tune-up of the boiler; and

- The types and amounts of fuels used over the 12 months prior to the tune-up of the boiler, but only if the unit was physically and legally capable of using more than one type of fuel during that period. Units sharing a fuel meter may estimate the fuel use by each unit. [40 C.F.R. § 63.11223(b)(6)]

- Compliance Report

For every two-year or five-year (as established by the boiler category listed above) compliance period, BGR shall prepare a compliance report by March 1st of the following year to document the information below for the two-year or five-year period. The report shall be maintained by the source and submitted to the Department and/or to the EPA upon request. The report must include the items contained in §§ 63.11225(b)(1) and (2), including the following: [40 C.F.R. § 63.11225(b)]

- Company name and address;

- A statement of whether the source has complied with all the relevant requirements of this Subpart;

- A statement certifying truth, accuracy, and completeness of the notification and signed by a responsible official and containing the official’s name, title, phone number, email address, and signature;

- The following certifications, as applicable:

- “This facility complies with the requirements in 40 C.F.R. § 63.11223 to conduct tune-ups of each boiler in accordance with the frequency specified in this Subpart.”

- “No secondary materials that are solid waste were combusted in any affected unit.”

- “This facility complies with the requirement in §§ 63.11214(d) and 63.11223(g) to minimize the boiler’s time spent during startup and shutdown and to conduct startups and shutdowns according to the manufacturer’s recommended procedures or procedures specified for a boiler of similar design if manufacturer’s recommended procedures are not available.”

- Recordkeeping

- Records shall be maintained consistent with the requirements of 40 C.F.R. Part 63, Subpart JJJJJJ including the following [40 C.F.R. § 63.11225(c)]:

- Copies of notifications and reports with supporting compliance documentation;

- Identification of each boiler, the date of tune-up, procedures followed for tune-up, and the manufacturer’s specifications to which the boiler was tuned;

- Records of the occurrence and duration of each malfunction of each applicable boiler; and

- Records of actions taken during periods of malfunction to minimize emissions, including corrective actions to restore the malfunctioning boiler.

- Records shall be in a form suitable and readily available for expeditious review. Each record must be kept for 5 years following the date of each recorded action. Each record must be kept on-site or be accessible from a central location by computer or other means that instantly provides access at the site for at least 2 years after the date of each recorded action. The records may be maintained off-site for the remaining 3 years. [40 C.F.R. § 63.11225(d)] Note: Standard Condition (8) of this license requires all records be retained for six years; therefore, the five-year record retention requirement of Subpart JJJJJJ is satisfied by compliance with the more stringent six-year requirement.

### Generators DAB-3, IAB-3, TF-1, and BLDG 600-1

BGR operates four existing emergency generators: Generator DAB-3, Generator IAB-3, Generator TF-1, and BLDG 600-1 Generator. The emergency generators are generator sets with each set consisting of an engine and an electrical generator. The emergency generators have engines rated at 5.9 MMBtu/hr, 4.7 MMBtu/hr, 1.68 MMBtu/hr, and 1.4 MMBtu/hr, respectively. All four engines fire distillate fuel. The emergency generators were manufactured in 2015, 2012, 1999, and 1992, respectively. The emission factors for Generators TF-1 and BLDG 600-1 were corrected to AP-42 and 06-096 C.M.R. ch. 115, BPT values based on their sizes being smaller than those for the standards originally applied.

##### BPT Findings

The BPT emission limits for Generators DAB-3 and IAB-3 are based on the following:

| PM/PM10/PM2.5 | – | 0.12 lb/MMBtu from 06-096 C.M.R. ch. 103 |
| --- | --- | --- |
| SO2 | – | Combustion of distillate fuel with a maximum sulfur content not to exceed 15 ppm (0.0015% sulfur by weight) |
| NOx | – | 3.2 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 |
| CO | – | 0.85 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 |
| VOC | – | 0.09 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BPT emission limits for Generators TF-1 and BLDG 600-1 are based on the following:

| PM/PM10/PM2.5 | – | 0.08 lb/MMBtu, 06-096 C.M.R. ch. 115, BPT |
| --- | --- | --- |
| SO2 | – | Combustion of distillate fuel with a maximum sulfur content not to exceed 15 ppm (0.0015% sulfur by weight) |
| NOx | – | 4.41 lb/MMBtu from AP-42 Table 3.3-1 dated 4/25 |
| CO | – | 0.95 lb/MMBtu from AP-42 Table 3.3-1 dated 4/25 |
| VOC | – | 0.36 lb/MMBtu from AP-42 Table 3.3-1 dated 4/25 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BPT emission limits for the generators are the following:

| Unit | Pollutant | lb/MMBtu |
| --- | --- | --- |
| Generator DAB-3 | PM | 0.12 |
| Generator IAB-3 | PM | 0.12 |

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator DAB-3 | 0.71 | 0.71 | 0.71 | 0.01 | 18.88 | 5.02 | 0.53 |
| Generator IAB-3 | 0.56 | 0.56 | 0.56 | 0.01 | 15.04 | 4.00 | 0.42 |
| Generator TF-1 | 0.20 | 0.20 | 0.20 | - | 7.41 | 1.6 | 0.60 |
| BLDG 600-1 Generator | 0.17 | 0.17 | 0.17 | - | 6.17 | 1.33 | 0.50 |

Visible Emissions for Generators DAB-3 and IAB-3

Visible emissions from Generators DAB-3 and IAB-3 shall each not exceed 20% opacity on a six-minute block average basis.

Visible Emissions for Generators TF-1 and BLDG 600-1

Visible emissions from Generators TF-1 and BLDG 600-1 shall each not exceed 20% opacity on a six-minute block average basis except for periods of startup during which time BGR shall either meet the normal operating visible emissions standard or the following work practice standards and alternative visible emissions standard.

- The duration of the startup shall not exceed 30 minutes per event;

- Visible emissions shall not exceed 50% opacity on a six-minute block average basis; and

- BGR shall keep records of the date, time, and duration of each startup.

Use of the work practice standards and alternative visible emissions standard in lieu of the normal operating standard is limited to no more than once per day.

Note: This does not limit the engine to one startup per day. It only limits the use of the alternative emission standard to once per day.

##### Chapter 169

Generators DAB-3, IAB-3, TF-1, and BLDG 600-1 were installed prior to the effective date of Stationary Generators, 06-096 C.M.R. ch. 169 and are therefore exempt from this rule pursuant to section 1.

##### New Source Performance Standards (NSPS)

Due to the dates of manufacture of the Generators TF-1 and BLDG 600-1, the engines are not subject to the New Source Performance Standards (NSPS) Standards of Performance for Stationary Compression Ignition Internal Combustion Engines (CI ICE), 40 C.F.R. Part 60, Subpart IIII (Subpart IIII) since the units were manufactured prior to April 1, 2006. [40 C.F.R. § 60.4200]

Subpart IIII is applicable to Generators DAB-3 and IAB-3 since the units were ordered after July 11, 2005, and manufactured after April 1, 2006. [40 C.F.R. § 60.4200]

A summary of the currently applicable federal 40 C.F.R. Part 60, Subpart IIII requirements is listed below.

- Emergency Engine Designation and Operating Criteria

Under 40 C.F.R. Part 60, Subpart IIII, a stationary reciprocating internal combustion engine (ICE) is considered an emergency stationary ICE (emergency engine) as long as the engine is operated in accordance with the following criteria. Operation of an engine outside of the criteria specified below may cause the engine to no longer be considered an emergency engine under 40 C.F.R. Part 60, Subpart IIII, resulting in the engine being subject to requirements applicable to non-emergency engines.

- Emergency Situation Operation (On-Site)

There is no operating time limit on the use of an emergency engine to provide electrical power or mechanical work during an emergency situation. Examples of use of an emergency engine during emergency situations include the following:

- Use of an engine to produce power for critical networks or equipment (including power supplied to portions of a facility) because of failure or interruption of electric power from the local utility (or the normal power source, if the facility runs on its own power production);

- Use of an engine to mitigate an on-site disaster;

- Use of an engine to pump water in the case of fire, flood, natural disaster, or severe weather conditions; and

- Similar instances.

- Non-Emergency Situation Operation

An emergency engine may be operated up to a maximum of 100 hours per calendar year for maintenance checks, readiness testing, and other non-emergency situations as described below.

- An emergency engine may be operated for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government; the manufacturer; the vendor; the regional transmission organization or equivalent balancing authority and transmission operator; or the insurance company associated with the engine. The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency ICE more than 100 hours per calendar year.

- An emergency engine may be operated for up to 50 hours per calendar year for other non-emergency situations. However, these operating hours are counted as part of the 100 hours per calendar year operating limit described in paragraph (2) and (2) (i) above.

The 50 hours per calendar year operating limit for other non-emergency situations cannot be used for peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 C.F.R. §§ 60.4211(f) and 60.4219]

    - 40 C.F.R. Part 60, Subpart IIII Requirements

- Manufacturer Certification Requirement

Generators DAB-3 and IAB-3 shall be certified by the manufacturer as meeting the emission standards for new nonroad compression ignition engines found in 40 C.F.R. § 60.4202. [40 C.F.R. § 60.4205(b)]

- Ultra-Low Sulfur Fuel Requirement

The fuel fired in the engines shall not exceed 15 ppm sulfur (0.0015% sulfur).

[40 C.F.R. § 60.4207(b)]

- Non-Resettable Hour Meter Requirement

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4209(a)]

- Operation and Maintenance Requirements

The engines shall be operated and maintained according to the manufacturer’s emission-related written instructions. BGR may only change those emission-related settings that are permitted by the manufacturer. [40 C.F.R. § 60.4211(a)]

BGR shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

- Annual Time Limit for Maintenance and Testing

As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). [40 C.F.R. § 60.4211(f)]

- Initial Notification Requirement

No initial notification is required under 40 C.F.R. Part 60, Subpart IIII for emergency engines. [40 C.F.R. § 60.4214(b)]

- Recordkeeping

BGR shall keep records that include the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time.

[40 C.F.R. § 60.4214(b)]

##### National Emission Standards for Hazardous Air Pollutants (NESHAP): 
40 C.F.R. Part 63, Subpart ZZZZ

Engines Subject to NSPS Subparts (Generators DAB-3 and IAB-3. described above)

Pursuant to 40 C.F.R. § 63.6590(c), stationary spark ignition and compression ignition engines subject to regulations under 40 C.F.R. Part 60, Subpart JJJJ (spark) and Subpart IIII (compression) must meet the requirements of Subpart ZZZZ by meeting the requirements of 40 C.F.R. Part 60, Subpart JJJJ or Subpart IIII, as applicable. No further requirements apply for such engines under Subpart ZZZZ. [40 C.F.R. § 63.6590(c)]

Engines Not Subject to NSPS Subparts (Generators TF-1 and BLDG 600-1, described above)

National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines, 40 C.F.R. Part 63, Subpart ZZZZ is applicable to Generators TF-1 and BLDG 600-1. The units are considered existing, emergency, stationary, reciprocating internal combustion engines at an area HAP source and are not subject to New Source Performance Standards regulations. EPA’s August 9, 2010 memo (Guidance Regarding Definition of Residential, Commercial, and Institutional Emergency Stationary RICE in the NESHAP for Stationary RICE) specifically does not exempt these units from the federal requirements. [40 C.F.R. § 63.6585]

A summary of the currently applicable federal 40 C.F.R. Part 63, Subpart ZZZZ requirements is listed below.

- Emergency Engine Designation and Operating Criteria

Under 40 C.F.R. Part 63, Subpart ZZZZ, a stationary reciprocating internal combustion engine (RICE) is considered an emergency stationary RICE (emergency engine) as long as the engine is operated in accordance with the following criteria. Operation of an engine outside of the criteria specified below may cause the engine to no longer be considered an emergency engine under 40 C.F.R. Part 63, Subpart ZZZZ, resulting in the engine being subject to requirements applicable to non-emergency engines.

- Emergency Situation Operation (On-Site)

There is no operating time limit on the use of an emergency engine to provide electrical power or mechanical work during an emergency situation. Examples of use of an emergency engine during emergency situations include the following:

- Use of an engine to produce power for critical networks or equipment (including power supplied to portions of a facility) because of failure or interruption of electric power from the local utility (or the normal power source, if the facility runs on its own power production);

- Use of an engine to mitigate an on-site disaster;

- Use of an engine to pump water in the case of fire, flood, natural disaster, or severe weather conditions; and

- Similar instances.

- Non-Emergency Situation Operation

An emergency engine may be operated up to a maximum of 100 hours per calendar year for maintenance checks, readiness testing, and other non-emergency situations as described below.

- An emergency engine may be operated for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government; the manufacturer; the vendor; the regional transmission organization or equivalent balancing authority and transmission operator; or the insurance company associated with the engine. The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency RICE more than 100 hours per calendar year.

- An emergency engine may be operated for up to 50 hours per calendar year for other non-emergency situations. However, these operating hours are counted as part of the 100 hours per calendar year operating limit described in paragraph (2) and (2) (i) above.

The 50 hours per calendar year operating limit for other non-emergency situations cannot be used for peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

Generators TF-1 and BLDG 600-1 shall be limited to the usage outlined in 40 C.F.R. § 63.6640(f) and therefore may be classified as existing emergency stationary RICE as defined in 40 C.F.R. Part 63, Subpart ZZZZ. Failure to comply with all of the requirements listed in 40 C.F.R. § 63.6640(f) may cause these engines to not be considered emergency engines and therefore subject to all applicable requirements for non-emergency engines.

- 40 C.F.R. Part 63, Subpart ZZZZ Requirements

- Operation and Maintenance Requirements

(40 C.F.R. § 63.6603(a) and Table 2(d))

|  | Operating Limitations |
| --- | --- |
| Compression ignition (distillate fuel) units: Generator TF-1 BLDG 600-1 Generator | - Change oil and filter every 500 hours of operation or within 1 year + 30 days of the previous change, whichever comes first; - Inspect the air cleaner every 1,000 hours of operation or within 1 year + 30 days of the previous inspection, whichever comes first, and replace as necessary; and - Inspect all hoses and belts every 500 hours of operation or within 1 year + 30 days of the previous inspection, whichever comes first, and replace as necessary. |

The engines shall be operated and maintained according to the manufacturer’s emission-related written instructions, or BGR shall develop a maintenance plan which must provide to the extent practicable for the maintenance and operation of the engines in a manner consistent with good air pollution control practice for minimizing emissions. [40 C.F.R. § 63.6625(e)]

- Optional Oil Analysis Program

BGR has the option of utilizing an oil analysis program which complies with the requirements of § 63.6625(i) in order to extend the specified oil change requirement. If this option is used, BGR must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for each engine. The analysis program must be part of the maintenance plan for each engine. [40 C.F.R. § 63.6625(i)]

- Non-Resettable Hour Meter Requirement

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 63.6625(f)]

- Startup Idle and Startup Time Minimization Requirements

During periods of startup the facility must minimize the engine’s time spent at idle and minimize the engine’s startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes. [40 C.F.R. § 63.6625(h) and 40 C.F.R. Part 63, Subpart ZZZZ Table 2d]

- Annual Time Limit for Maintenance and Testing

As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). [40 C.F.R. § 63.6640(f)]

- Recordkeeping

BGR shall keep records that include maintenance conducted on the engines and the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time. [40 C.F.R. § 63.6655(f)]

### Generators IAB-4 and 99-1

BGR proposes to install an additional emergency generator, Generator IAB-4. The emergency generator is a generator set consisting of an engine and an electrical generator. Generator IAB-4 has an engine rated at 21.2 MMBtu/hr which fires distillate fuel. The emergency generator was manufactured in 2025. The engine is US EPA Tier 2 certified, 16-cylinder Mitsubishi engine, with an output capacity of 2,000 kW.

Generator 99-1 is rated at 3.75 MMBtu/hr (approximately 540 hp) and fires distillate fuel. The unit was manufactured in 2020 and is operated to provide back-up power to runway lighting. This operational scenario, called into operation in response to certain weather conditions, does not always constitute emergency use as defined in 40 C.F.R. Part 60, Subpart III or Part 63, Subpart ZZZZ, except for periods of time when line power loss to the facility occurs. BGR shall maintain records sufficient to document hours of operation consistent with that defined for emergency use in the applicable federal engine rules, hours of operation outside of that definition, and the reason for operation each time.

##### BACT Findings

The BACT emission limits for Generators IAB-4 and 99-1 are based on the following:

| PM/PM10/PM2.5 | – | 0.12 lb/MMBtu, 06-096 C.M.R. ch. 103 |
| --- | --- | --- |
| SO2 | – | Combustion of distillate fuel with a maximum sulfur content not to exceed 15 ppm (0.0015% sulfur by weight) |
| NOx | – | 3.2 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 (for those units with heat inputs of 4.2 MMBtu/hr or greater); 4.41 lb/MMBtu from AP-42 Table 3.3-1 dated 4/25 (for those units with heat inputs less than 4.2 MMBtu/hr) |
| CO | – | 0.85 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 (for those units with heat inputs of 4.2 MMBtu/hr or greater); 0.95 lb/MMBtu from AP-42 Table 3.3-1 dated 4/25 (for those units with heat inputs less than 4.2 MMBtu/hr) |
| VOC | – | 0.09 lb/MMBtu from AP-42 Table 3.4-1 dated 4/25 (for those units with heat inputs of 4.2 MMBtu/hr or greater); 0.36 lb/MMBtu from AP-42 Table 3.3-1 dated 4/25 (for those units with heat inputs less than 4.2 MMBtu/hr) |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

The BACT emission limits for Generators IAB-4 and 99-1 are the following:

| Unit | Pollutant | lb/MMBtu |
| --- | --- | --- |
| Generator IAB-4 | PM | 0.12 |
| Generator 99-1 | PM | 0.12 |

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator IAB-4 | 2.55 | 2.55 | 2.55 | 0.03 | 67.97 | 18.05 | 1.91 |
| Generator 99-1 | 0.45 | 0.45 | 0.45 | 0.01 | 16.54 | 3.56 | 1.35 |

Visible emissions from Generators IAB-4 and 99-1 shall each not exceed 20% opacity on a six-minute block average basis.

BACT for each emergency generator includes recordkeeping of all maintenance conducted on the engine.

##### Chapter 169

Generator 99-1 was installed prior to the effective date of Stationary Generators, 06-096 C.M.R. ch. 169 (Chapter 169), and is therefore exempt from this rule pursuant to section 1.

Chapter 169 is applicable to Generator IAB-4. It is an emergency generator powered by an engine with a rated output of greater than 1,000 brake horsepower (747 kW). Chapter 169 identifies emission standards for generator engines subject to this chapter and stack height requirements for certain generator engines subject to this chapter.

- Chapter 169 Emission Standards Requirements

For Generator IAB-4, BGR has elected to comply with the emission standards for emergency generators by accepting a limit on total generator usage (emergency and non-emergency combined) of 500 hours/year (12-month rolling total basis). Compliance shall be demonstrated through recordkeeping of all generator operating times.

If there are periods of extended outage such as a natural disaster or other similar event outside BGR’s control, BGR may apply to the Department for a temporary variance to exempt specific time periods from this annual hour limit. The Department Commissioner may, without hearing, issue that variance for a period of time not to exceed 30 days if, in his/her judgement, the variance is necessary to avoid immediate threat to public health, safety, or general welfare or to protect critical infrastructure.

- Chapter 169 Stack Height Requirements

Chapter 169 identifies stack height requirements for any stack used to exhaust a generator engine or combination of generator engines with a combined rated output equal to or greater than 1,000 brake horsepower (747 kW). Individual generator engines with a maximum power capacity of less than 300 kW are not included in the assessment of the combined generator power capacity exhausted through a common stack. [06-096 C.M.R. ch. 169, § 6]

BGR submitted a qualitative ambient impact screening analysis (QAISA) for Generator IAB-4. The QAISA considered many factors including engine size, emission rates, operational limits, stack height, height of surrounding structures, distance to ambient air, terrain features, and proximity to sensitive receptors. Based on the analysis submitted, the Department finds that the proposed minimum stack height of 15 feet above ground level is not likely to cause or contribute to violations of ambient air quality standards. [06-096 C.M.R. ch. 169, § 6(B)]

##### New Source Performance Standards

Standards of Performance for Stationary Compression Ignition Internal Combustion Engines, 40 C.F.R. Part 60, Subpart IIII is applicable to Generator IAB-4 and Generator 99-1 since the units were ordered after July 11, 2005, and manufactured after April 1, 2006. [40 C.F.R. § 60.4200]

A summary of the currently applicable federal 40 C.F.R. Part 60, Subpart IIII requirements is listed below.

- Emergency Engine Designation and Operating Criteria

Under 40 C.F.R. Part 60, Subpart IIII, a stationary reciprocating internal combustion engine (ICE) is considered an emergency stationary ICE (emergency engine) as long as the engine is operated in accordance with the following criteria. Operation of an engine outside of the criteria specified below may cause the engine to no longer be considered an emergency engine under 40 C.F.R. Part 60, Subpart IIII, resulting in the engine being subject to requirements applicable to non-emergency engines.

- Emergency Situation Operation (On-Site)

Examples of use of an emergency engine during emergency situations include the following:

- Use of an engine to produce power for critical networks or equipment (including power supplied to portions of a facility) because of failure or interruption of electric power from the local utility (or the normal power source, if the facility runs on its own power production);

- Use of an engine to mitigate an on-site disaster;

- Use of an engine to pump water in the case of fire, flood, natural disaster, or severe weather conditions; and

- Similar instances.

- Non-Emergency Situation Operation

An emergency engine may be operated up to a maximum of 100 hours per calendar year for maintenance checks, readiness testing, and other non-emergency situations as described below.

- An emergency engine may be operated for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government; the manufacturer; the vendor; the regional transmission organization or equivalent balancing authority and transmission operator; or the insurance company associated with the engine. The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency ICE more than 100 hours per calendar year.

- An emergency engine may be operated for up to 50 hours per calendar year for other non-emergency situations. However, these operating hours are counted as part of the 100 hours per calendar year operating limit described in paragraph (2) and (2) (i) above.

The 50 hours per calendar year operating limit for other non-emergency situations cannot be used for peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 C.F.R. §§ 60.4211(f) and 60.4219]

- 40 C.F.R. Part 60, Subpart IIII Requirements

- Manufacturer Certification Requirement

The engine shall be certified by the manufacturer as meeting the emission standards for new nonroad compression ignition engines found in 40 C.F.R. § 60.4202. [40 C.F.R. § 60.4205(b)] A certificate of conformity was submitted with this application for Generator IAB-4. A picture of the label on Generator 99-1, showed serial number PW301174 was in compliance as an emergency generator.

- Ultra-Low Sulfur Fuel Requirement

The fuel fired in Generators IAB-4 and 99-1 shall not exceed 15 ppm sulfur (0.0015% sulfur). [40 C.F.R. § 60.4207(b)]

- Non-Resettable Hour Meter Requirement

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4209(a)]

- Operation and Maintenance Requirements

Each engine shall be operated and maintained according to the manufacturer’s emission-related written instructions. BGR may only change those emission-related settings that are permitted by the manufacturer. [40 C.F.R. § 60.4211(a)]

BGR shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

- Annual Time Limit for Maintenance and Testing

As an emergency engine, the unit shall be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). [40 C.F.R. § 60.4211(f)]

- Initial Notification Requirement

No initial notification is required under 40 C.F.R. Part 60, Subpart IIII for emergency engines. [40 C.F.R. § 60.4214(b)]

- Recordkeeping

BGR shall keep records that include the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time.

[40 C.F.R. § 60.4214(b)]

For simplicity, the recordkeeping described above for Generator IAB-4 is streamlined with the more stringent recordkeeping required to demonstrate compliance with 06-096 C.M.R. ch. 169. The standards themselves are not being streamlined, only the recordkeeping required for compliance demonstration. Therefore, BGR shall maintain records of engine operating times on a 12-month rolling total basis. The 12-month rolling total encompassing January through December of each calendar year shall be used to demonstrate compliance with the annual time limit for maintenance and testing pursuant to 40 C.F.R. § 60.4211(f) as described above.

- National Emission Standards for Hazardous Air Pollutants (NESHAP): 40 C.F.R. Part 63, Subpart ZZZZ

Pursuant to 40 C.F.R. § 63.6590(c), stationary combustion ignition engines subject to regulations under 40 C.F.R. Part 60, Subpart IIII must meet the requirements of Subpart ZZZZ by meeting the requirements of 40 C.F.R. Part 60, Subpart IIII. No further requirements apply for such engines under Subpart ZZZZ. [40 C.F.R. § 63.6590(c)]

### Snow Melter #1

BGR operates one portable snow melter designed to remove accumulated snow from the runway. Snow is loaded into a melting tank with a burner system capable of firing up to 64 gallons per hour of distillate fuel, equivalent to approximately 8.96 MMBtu/hr. The unit is used periodically through the winter season, as needed. Due to the size and periodic use of the unit, BPT for the snow melter shall be the following:

- Snow Melter #1 shall fire distillate fuel with a maximum fuel sulfur content of 0.0015% by weight.

- Snow Melter #1 shall be limited to 200 hours of operation per calendar year.

- Emission limits for Snow Melter #1 are based on the following:

| PM/PM10/PM2.5 | – | 0.12 lb/MMBtu/hr, 06-096 C.M.R. ch. 103 |
| --- | --- | --- |
| SO2 | – | Combustion of distillate fuel with a maximum sulfur content not to exceed 15 ppm (0.0015% sulfur by weight) |
| NOx | – | 20 lb/1,000 gal based on AP-42 Table 1.3-1 dated 5/10 |
| CO | – | 5 lb/1,000 gal based on AP-42 Table 1.3-1 dated 5/10 |
| VOC | – | 0.34 lb/1,000 gal based on AP-42 Table 1.3-3 dated 5/10 |
| Visible Emissions | – | 06-096 C.M.R. ch. 101 |

- Emissions from Snow Melter #1 shall not exceed the following:

| Unit | Pollutant | lb/MMBtu | Origin and Authority |
| --- | --- | --- | --- |
| Snow Melter #1 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT]:

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Snow Melter #1 | 1.08 | 1.08 | 1.08 | 0.01 | 1.28 | 0.32 | 0.02 |

- Visible emissions from the snow melter shall not exceed 10% opacity on a six-minute block average basis.

### Volatile Organic Liquid Storage Tanks

BGR operates five above ground storage tanks that contain volatile organic liquids. Tanks T-1, T-2, and T-3 store Jet A fuel with capacities of 630,000 gallons, 2,000,000 gallons, and 630,000 gallons, respectively. T-4 and T-5 store aviation gasoline and on-road gasoline with capacities of 12,000 gallons each.

- 06-096 C.M.R. ch. 111

Tanks T-1, T-2, and T-3 are not subject to the requirements of Petroleum Liquid Storage Vapor Control, 06-096 C.M.R. ch. 111 (Ch. 111), because they store a product with a vapor pressure less than 10.5 kilopascals. Tanks T-4 and T-5 are not subject to Ch. 111 because they have tank capacities less than 39,000 gallons.

- 06-096 C.M.R. ch. 118

Tanks T-1, T-2, and T-3 are not subject to the requirements of Gasoline Dispensing Facilities Vapor Control, 06-096 C.M.R. ch. 118 (Ch. 118), because they do not store gasoline.

Tank T-4 is not subject to Ch. 118 because it stores aviation gasoline, which is not subject to this chapter. [06-096 C.M.R. ch. 118 § 2(B)]

Tank T-5 is not subject to Stage I provisions of Ch. 118 because its throughput is less than 10,000 gallons per month. However, pursuant to § B(1) of this chapter, any gasoline dispensing facility, regardless of throughput, is subject to the requirements of Sections 4(A) and 10(B) of this Chapter. Applicable requirements from Sections 4(A) and 10(B) of Ch. 118 are as follows:

- BGR shall maintain fill pipes which extend to the bottom of each of Tanks T-4 and T-5 within six inches of the bottom of the stationary gasoline storage tank. [06-096 C.M.R. ch. 118, § 4(A) for Tanks T-5; 06-096 C.M.R. ch. 115, BPT for Tank T-4]

- BGR shall maintain gasoline throughput records that will allow the monthly and annual throughput of Tanks T-4 and T-5 to be determined. [06-096 C.M.R. ch. 118, § 10(B) for Tank T-5; 06-096 C.M.R. ch. 115, BPT for Tank T-4]

- 06-096 C.M.R. ch. 133

Tanks T-1, T-2, T-3, T-4, and T-5 are not subject to the requirements of Petroleum Liquids Transfer Vapor Recovery at Bulk Gasoline Plants, 06-096 C.M.R. ch. 133, because BGR is not a bulk gasoline plant (as defined by 06-096 C.M.R. ch. 100).

- 06-096 C.M.R. ch. 170

Tanks T-1, T-2, T-3, T-4, and T-5 are not subject to the requirements of Degassing of Petroleum Storage Tanks, Marine Vessels, and Transport Vessels, 06-096 C.M.R. ch. 170 because BGR is not a petroleum storage facility as defined by the rule.

- 06-096 C.M.R. ch. 171

Tanks T-1, T-2, T-3, T-4, and T-5 are not subject to the requirements of Control of Petroleum Storage Facilities, 06-096 C.M.R. ch. 171, because BGR is not a petroleum storage facility as defined by the rule.

- 40 C.F.R. Part 60, Subpart Kb

Tanks T-1, T-2, and T-3 are not subject to the requirements of Standards of Performance for Volatile Organic Liquid Storage Vessels (Including Petroleum Liquid Storage Vessels) for which Construction, Reconstruction, or Modification Commenced After July 23, 1984, and On or Before October 4, 2023, 40 C.F.R. Part 60, Subpart Kb (Subpart Kb), because the true vapor pressure of the product stored is less than 15.0 kilopascals. [40 C.F.R. § 60.110b(b)]

Tanks T-4 and T-5 are exempt from Subpart Kb since their storage capacity is each less than 19,812 gallons.

- 40 C.F.R. Part 60, Subpart Kc

Tanks T-1, T-2, T-3, T-4, and T-5 are not subject to the requirements of Standards of Performance for Volatile Organic Liquid Storage Vessels (Including Petroleum Liquid Storage Vessels) for which Construction, Reconstruction, or Modification Commenced After October 4, 2023, 40 C.F.R. Part 60, Subpart Kc (Subpart Kc).

Tanks T-1, T-2, T-3, T-4, and T-5 were installed prior to October 15, 2024. Existing storage vessels can become subject to Subpart Kc if modified. Pursuant to 40 C.F.R. § 60.110c(e), a modification occurs if the storage vessel is used to store a volatile organic liquid (VOL) that has a greater maximum true vapor pressure than all VOL historically stored or permitted to be stored in it. T-1, T-2, and T-3 have historically stored Jet A fuel and is limited to only storing Jet A fuel. Therefore, T-1, T-2, and T-3 are not subject to Subpart Kc provided they each continue to store the products for which they are currently licensed. BGR shall maintain records of the type and maximum true vapor pressure for each product stored in T-1, T-2, and T-3.

- BPT for Tanks T-1, T-2, T-3, T-4, and T-5

- Tanks T-1, T-2, and T-3 shall only contain Jet A fuel.

- Tank T-4 shall only contain Low Lead Aviation Gasoline.

- Tank T-5 shall only contain Gasoline.

- BGR shall keep records of tank throughput for each tank on a calendar year basis.

- VOC emissions from these tanks shall be conservatively estimated using TANKS 4.0 (an older version of the EPA’s TANKS Emissions Estimation Software, based on AP-42 emission factors and formulas from Compilation of Air Emissions Factors from Stationary Sources, AP-42, Volume I, Chapter 7) and the tank dimensions and throughputs from A-906-71-A-N (which contain higher throughputs than the current quantities reported in 2024).

BGR shall keep records showing the dimensions of Tanks T-4 and T-5 and analyses showing the capacities of the storage vessels. These records shall be kept for the life of the tanks and be readily available upon request.

### General Process Emissions

Visible emissions from any general process source shall not exceed 20% opacity on a six-minute block average basis.

### Fugitive Emissions

BGR shall not cause emissions of any fugitive dust during any period of construction, reconstruction, or operation without taking reasonable precautions. Such reasonable precautions shall be included in the facility’s continuing program of best management practices for suppression of fugitive particulate matter. See 06-096 C.M.R. ch. 101, § 4(C) for a list of potential reasonable precautions.

BGR shall not cause or allow visible emissions within 20 feet of ground level, measured as any level of opacity and not including water vapor, beyond the legal boundary of the property on which such emissions occur. Compliance with this standard shall be determined pursuant to 40 C.F.R. Part 60, Appendix A, Method 22.

### Annual Emissions

The table below provides an estimate of facility-wide annual emissions for the purposes of calculating the facility’s annual air license fee and establishing the facility’s potential to emit (PTE). Only licensed equipment is included, i.e., emissions from insignificant activities are excluded. Similarly, unquantifiable fugitive particulate matter emissions are not included except when required by state or federal regulations. Maximum potential emissions were calculated based on the following:

- 200 hours per year of operation of the snow melter and 100 hours per year each of non-emergency operation for Generators DAB-3, IAB-3, IAB-4, 99-1, TF-1, and BLDG 600-1; and

- Maximum heat input of 98,000 MMBtu in the 15 boilers addressed in this license, combined, on a calendar year basis.

Emissions from the boilers are calculated based on the worst-case scenario of firing 139,286 gallons of Jet A fuel (licensed maximum) and the balance (to total the equivalent of 98,000 MMBtu/year) of distillate fuel for PM, SO2, and NOx and firing natural gas for CO and VOC.

This information does not represent a comprehensive list of license restrictions or permissions. That information is provided in the Order section of this license.

Total Licensed Annual Emissions for the Facility

Tons/year

(used to calculate the annual license fee)

|  | PM | PM10 | PM2.5 | SO2 | NOx | CO | VOC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boilers | 5.9 | 5.9 | 5.9 | 14.8 | 7.0 | 4.0 | 0.3 |
| Snow Melter | 0.1 | 0.1 | 0.1 | - | 0.1 | - | - |
| Emergency Generators | 0.2 | 0.2 | 0.2 | - | 6.6 | 1.7 | 0.3 |
| Storage Tanks | - | - | - | - | - | - | 2.3 |
| Total TPY | 6.2 | 6.2 | 6.2 | 14.8 | 13.7 | 5.7 | 2.9 |

| Pollutant | Tons/year |
| --- | --- |
| Single HAP | 7.9 |
| Total HAP | 19.9 |

## AMBIENT AIR QUALITY ANALYSIS

The level of ambient air quality impact modeling required for a minor source is determined by the Department on a case-by-case basis. In accordance with 06-096 C.M.R. ch. 115, an ambient air quality impact analysis is not required for a minor source if the total licensed annual emissions of any pollutant released do not exceed the following levels and there are no extenuating circumstances:

| Pollutant | Tons/Year |
| --- | --- |
| PM10 | 25 |
| PM2.5 | 15 |
| SO2 | 50 |
| NOx | 50 |
| CO | 250 |

The total licensed annual emissions for the facility are below the emission levels contained in the table above and there are no extenuating circumstances; therefore, an ambient air quality impact analysis is not required as part of this license.

This determination is based on information provided by the applicant regarding the expected construction and operation of the proposed and currently licensed emission units. If the Department determines that any parameter (e.g., stack size, configuration, flow rate, emission rates, nearby structures, etc.) deviates from what was included in the application, the Department may require BGR to submit additional information and may require an ambient air quality impact analysis at that time.

# ORDER

Based on the above Findings and subject to conditions listed below, the Department concludes that the emissions from this source:

- will receive Best Practical Treatment,

- will not violate applicable emission standards, and

- will not violate applicable ambient air quality standards in conjunction with emissions from other sources.

The Department hereby grants Air Emission License A-906-71-J-R/A subject to the following conditions.

Severability. The invalidity or unenforceability of any provision of this License or part thereof shall not affect the remainder of the provision or any other provisions. This License shall be construed and enforced in all respects as if such invalid or unenforceable provision or part thereof had been omitted.

## STANDARD CONDITIONS

- Employees and authorized representatives of the Department shall be allowed access to the licensee’s premises during business hours, or any time during which any emissions units are in operation, and at such other times as the Department deems necessary for the purpose of performing tests, collecting samples, conducting inspections, or examining and copying records relating to emissions (38 M.R.S. § 347-C).

- The licensee shall acquire a new or amended air emission license prior to beginning actual construction of a modification, unless specifically provided for in Chapter 115.

[06-096 C.M.R. ch. 115]

- Approval to construct shall become invalid if the source has not commenced construction within eighteen (18) months after receipt of such approval or if construction is discontinued for a period of eighteen (18) months or more. The Department may extend this time period upon a satisfactory showing that an extension is justified, but may condition such extension upon a review of either the control technology analysis or the ambient air quality standards analysis, or both. [06-096 C.M.R. ch. 115]

- The licensee shall establish and maintain a continuing program of best management practices for suppression of fugitive particulate matter during any period of construction, reconstruction, or operation which may result in fugitive dust, and shall submit a description of the program to the Department upon request. [06-096 C.M.R. ch. 115]

- The licensee shall pay the annual air emission license fee to the Department, calculated pursuant to Title 38 M.R.S. § 353-A. [06-096 C.M.R. ch. 115] Payment of the annual air emission license fee for BGR is due by the end of February of each year. [38 M.R.S. § 353-A(3)]

- The license does not convey any property rights of any sort, or any exclusive privilege. [06-096 C.M.R. ch. 115]

- The licensee shall maintain and operate all emission units and air pollution systems required by the air emission license in a manner consistent with good air pollution control practice for minimizing emissions. [06-096 C.M.R. ch. 115]

- The licensee shall maintain sufficient records to accurately document compliance with emission standards and license conditions and shall maintain such records for a minimum of six (6) years. The records shall be submitted to the Department upon written request. [06-096 C.M.R. ch. 115]

- The licensee shall comply with all terms and conditions of the air emission license. The filing of an appeal by the licensee, the notification of planned changes or anticipated noncompliance by the licensee, or the filing of an application by the licensee for a renewal of a license or amendment shall not stay any condition of the license.

[06-096 C.M.R. ch. 115]

- The licensee may not use as a defense in an enforcement action that the disruption, cessation, or reduction of licensed operations would have been necessary in order to maintain compliance with the conditions of the air emission license.

[06-096 C.M.R. ch. 115]

- In accordance with the Department’s air emission compliance test protocol and 40 C.F.R. Part 60 or other method approved or required by the Department, the licensee shall:

- Perform stack testing to demonstrate compliance with the applicable emission standards under circumstances representative of the facility’s normal process and operating conditions:

- Within sixty (60) calendar days of receipt of a notification to test from the Department or EPA, if visible emissions, equipment operating parameters, staff inspection, air monitoring or other cause indicate to the Department that equipment may be operating out of compliance with emission standards or license conditions; or

- Pursuant to any other requirement of this license to perform stack testing.

- Install or make provisions to install test ports that meet the criteria of 40 C.F.R. Part 60, Appendix A, and test platforms, if necessary, and other accommodations necessary to allow emission testing; and

- Submit a written report to the Department within thirty (30) days from date of test completion.

[06-096 C.M.R. ch. 115]

- If the results of a stack test performed under circumstances representative of the facility’s normal process and operating conditions indicate emissions in excess of the applicable standards, then:

- Within thirty (30) days following receipt of the written test report by the Department, or another alternative timeframe approved by the Department, the licensee shall re-test the non-complying emission source under circumstances representative of the facility’s normal process and operating conditions and in accordance with the Department’s air emission compliance test protocol and 40 C.F.R. Part 60 or other method approved or required by the Department; and

- The days of violation shall be presumed to include the date of stack test and each and every day of operation thereafter until compliance is demonstrated under normal and representative process and operating conditions, except to the extent that the facility can prove to the satisfaction of the Department that there were intervening days during which no violation occurred or that the violation was not continuing in nature; and

- The licensee may, upon the approval of the Department following the successful demonstration of compliance at alternative load conditions, operate under such alternative load conditions on an interim basis prior to a demonstration of compliance under normal and representative process and operating conditions.

[06-096 C.M.R. ch. 115]

- Notwithstanding any other provisions in the State Implementation Plan approved by the EPA or Section 114(a) of the CAA, any credible evidence may be used for the purpose of establishing whether a person has violated or is in violation of any statute, regulation, or license requirement. [06-096 C.M.R. ch. 115]

- The licensee shall maintain records of malfunctions, failures, downtime, and any other similar change in operation of air pollution control systems or the emissions unit itself that would affect emissions and that is not consistent with the terms and conditions of the air emission license. The licensee shall notify the Department within two (2) days or the next state working day, whichever is later, of such occasions where such changes result in an increase of emissions. The licensee shall report all excess emissions in the units of the applicable emission limitation. [06-096 C.M.R. ch. 115]

- Upon written request from the Department, the licensee shall establish and maintain such records, make such reports, install, use and maintain such monitoring equipment, sample such emissions (in accordance with such methods, at such locations, at such intervals, and in such a manner as the Department shall prescribe), and provide other information as the Department may reasonably require to determine the licensee’s compliance status.

[06-096 C.M.R. ch. 115]

- The licensee shall notify the Department within 48 hours and submit a report to the Department on a quarterly basis if a malfunction or breakdown in any component causes a violation of any emission standard. [38 M.R.S. § 605]

## SPECIFIC CONDITIONS

#### Boilers IAB-1, IAB-2, DAB-1A, 461-1, 462-1, 463-1, 464-1, 457-1, 268-1, 271-1, 253-2, 96-1, 100-1, 100-2, and 269-1

- Fuel [06-096 C.M.R. ch. 115, BPT]

- BGR shall not exceed a total limit of 98,000 MMBtu equivalent from firing distillate fuel, Jet A fuel, and natural gas in the 15 boilers addressed in this license, on a calendar year total basis. Compliance shall be demonstrated by tracking fuel usage and calculated using the following fuel heat content factors:

Distillate fuel – 0.14 MMBtu/gallon

Jet A fuel – 0.14 MMBtu/gallon

Natural Gas – 1,030 Btu/scf

Records of annual fuel use shall be kept on a monthly and calendar year basis.

- The facility shall not purchase or otherwise obtain distillate fuel with a maximum sulfur content that exceeds 0.0015% by weight (15 ppm).

- Compliance with distillate fuel requirements shall be demonstrated by fuel records showing the quantity, type, and the percent sulfur of the fuel delivered (if applicable). Records of annual fuel use shall be kept on a monthly and 12-month rolling total basis. Fuel sulfur content compliance shall be demonstrated by fuel delivery receipts from the supplier, a statement from the supplier that the fuel delivered meets Maine’s fuel sulfur content standards, certificate of analysis, or testing of fuel in the tank on-site.

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT/BACT]:

| Emission Unit | Fuel Type | Pollutant | lb/MMBtu |
| --- | --- | --- | --- |
| Boiler IAB-1 | Distillate Fuel | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler IAB-2 | Distillate Fuel | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler DAB-1A | Distillate Fuel | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 461-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 462-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 463-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |
| Boiler 464-1 | Distillate and Jet A Fuels | PM | 0.12 |
|  | Natural Gas | PM | 0.05 |

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT/BACT]:

| Emission Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boiler IAB-1 | 0.50 | 0.50 | 0.50 | 0.01 | 0.60 | 0.34 | 0.02 |
| Boiler IAB-2 | 0.50 | 0.50 | 0.50 | 0.01 | 0.60 | 0.34 | 0.02 |
| Boiler DAB-1A | 0.73 | 0.73 | 0.73 | 0.01 | 0.87 | 0.50 | 0.03 |
| Boiler 461-1 | 0.76 | 0.76 | 0.76 | 9.52 | 0.90 | 0.51 | 0.03 |
| Boiler 462-1 | 0.73 | 0.73 | 0.73 | 9.25 | 0.87 | 0.50 | 0.03 |
| Boiler 463-1 | 0.73 | 0.73 | 0.73 | 9.25 | 0.87 | 0.50 | 0.03 |
| Boiler 464-1 | 0.75 | 0.75 | 0.75 | 9.49 | 0.90 | 0.51 | 0.03 |
| Boiler 457-1 | 0.33 | 0.33 | 0.33 | - | 0.40 | 0.23 | 0.01 |
| Boiler 268-1 | 0.33 | 0.33 | 0.33 | - | 0.40 | 0.23 | 0.01 |
| Boiler 271-1 | 0.18 | 0.18 | 0.18 | - | 0.21 | 0.12 | 0.01 |
| Boiler 253-2 | 0.08 | 0.08 | 0.08 | - | 0.16 | 0.14 | 0.01 |
| Boiler 96-1 | 0.18 | 0.18 | 0.18 | - | 0.21 | 0.12 | 0.01 |
| Boiler 100-1 | 0.33 | 0.33 | 0.33 | - | 0.40 | 0.23 | 0.01 |
| Boiler 100-2 | 0.34 | 0.34 | 0.34 | - | 0.40 | 0.23 | 0.01 |
| Boiler 269-1 | 0.19 | 0.19 | 0.19 | - | 0.23 | 0.13 | 0.01 |

- During periods of time when distillate fuel or Jet A fuel is being fired, visible emissions from each of the existing boilers shall not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(2)]

- During periods of time when natural gas is being fired, visible emissions from each of the existing boilers shall not exceed 10% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(3)]

- BGR shall comply with all requirements of 40 C.F.R. Part 63, Subpart JJJJJJ applicable to Boilers IAB-1, IAB-2, DAB-1A, 461-1, 462-1, 463-1, 464-1, 457-1, 268-1, 271-1, 253-2, 100-1, and 100-2 including, but not limited to, the following: 
[incorporated under 06-096 C.M.R. ch. 115, BPT/BACT]

- The facility shall implement a boiler tune-up program. [40 C.F.R. § 63.11223]

- Each tune-up shall be conducted at a frequency specified by the rule and based on the size, age, and operations of the boiler. See chart below:

| Boiler Category | Tune-Up Frequency |
| --- | --- |
| New or Existing Oil, Biomass and Coal fired boilers that are not designated as "Boilers with less frequent tune up requirements" listed below (Boiler DAB-1A, Boiler 461-1, Boiler 462-1, Boiler 463-1, Boiler 464-1) | Every 2 years |
| Oil fired boilers with a heat input capacity of ≤5MMBtu/hr (Boiler IAB-1, Boiler IAB-2, Boiler 457-1, Boiler 268-1, Boiler 271-1, Boiler 253-2, Boiler 100-1, Boiler 100-2) | Every 5 years |

[40 C.F.R. § 63.11223(a) and Table 2]

- The boiler tune-up program, conducted to demonstrate continuous compliance, shall be performed as specified below:

- As applicable, inspect the burner, and clean or replace any component of the burner as necessary. Delay of the burner inspection until the next scheduled shutdown is permitted, not to exceed 36 months from the previous inspection. Delay of the burner inspection until the next scheduled shutdown is permitted for up to 72 months from the previous inspection for oil fired boilers less than or equal to 5 MMBtu/hour. [40 C.F.R. § 63.11223(b)(1)]

- Inspect the flame pattern, as applicable, and adjust the burner as necessary to optimize the flame pattern, consistent with the manufacturer’s specifications. [40 C.F..R § 63.11223(b)(2)]

- Inspect the system controlling the air-to-fuel ratio, as applicable, and ensure it is correctly calibrated and functioning properly. Delay of the inspection until the next scheduled shutdown is permitted, not to exceed 36 months from the previous inspection. Delay of the inspection until the next scheduled shutdown is permitted for up to 72 months from the previous inspection for oil fired boilers less than or equal to 5 MMBtu/hour. [40 C.F.R. § 63.11223(b)(3)]

- Optimize total emissions of CO, consistent with manufacturer’s specifications. [40 C.F.R. § 63.11223(b)(4)]

- Measure the concentration in the effluent stream of CO in parts per million by volume (ppmv), and oxygen in volume percent, before and after adjustments are made (measurements may be either on a dry or wet basis, as long as it is the same basis before and after the adjustments are made). Measurements may be taken using a portable CO analyzer.

[40 C.F.R. § 63.11223(b)(5)]

- If a unit is not operating on the required date for a tune-up, the tune-up must be conducted within 30 days of start-up.

[40 C.F.R. § 63.11223(b)(7)]

- Tune-Up Report: A tune-up report shall be maintained onsite and submitted to the Department and EPA upon request. The report shall contain the following information:

- The concentration of CO in the effluent stream (ppmv) and oxygen (volume percent) measured at high fire or typical operating load both before and after the boiler tune-up;

- A description of any corrective actions taken as part of the tune-up of the boiler; and

- The types and amounts of fuels used over the 12 months prior to the tune-up of the boiler, but only if the unit was physically and legally capable of using more than one type of fuel during that period. Units sharing a fuel meter may estimate the fuel use by each unit. [40 C.F.R. § 63.11223(b)(6)]

- Compliance Report

For every two-year or five-year (as established by the boiler category listed above) compliance period, BGR shall prepare a compliance report shall be prepared by March 1st of the following year to document the information below for the two-year or five-year period. The report shall be maintained by the source and submitted to the Department and/or to the EPA upon request. The report must include the items contained in §§ 63.11225(b)(1) and (2), including the following: [40 C.F.R. § 63.11225(b)]

- Company name and address;

- A statement of whether the source has complied with all the relevant requirements of this Subpart;

- A statement certifying truth, accuracy, and completeness of the notification and signed by a responsible official and containing the official’s name, title, phone number, email address, and signature;

- The following certifications, as applicable:

- “This facility complies with the requirements in 40 C.F.R. § 63.11223 to conduct tune-ups of each boiler in accordance with the frequency specified in this Subpart.”

- “No secondary materials that are solid waste were combusted in any affected unit.”

- “This facility complies with the requirement in §§ 63.11214(d) and 63.11223(g) to minimize the boiler’s time spent during startup and shutdown and to conduct startups and shutdowns according to the manufacturer’s recommended procedures or procedures specified for a boiler of similar design if manufacturer’s recommended procedures are not available.”

- Recordkeeping

- Records shall be maintained consistent with the requirements of 40 C.F.R. Part 63, Subpart JJJJJJ including the following [40 C.F.R. § 63.11225(c)]:

- Copies of notifications and reports with supporting compliance documentation;

- Identification of each boiler, the date of tune-up, procedures followed for tune-up, and the manufacturer’s specifications to which the boiler was tuned;

- Records of the occurrence and duration of each malfunction of each applicable boiler; and

- Records of actions taken during periods of malfunction to minimize emissions, including corrective actions to restore the malfunctioning boiler.

- Records shall be in a form suitable and readily available for expeditious review. Each record must be kept for 5 years following the date of each recorded action. Each record must be kept on-site or be accessible from a central location by computer or other means that instantly provides access at the site for at least 2 years after the date of each recorded action. The records may be maintained off-site for the remaining 3 years. [40 C.F.R. § 63.11225(d)] Note: Standard Condition (8) of this license requires all records be retained for six years; therefore, the five-year record retention requirement of Subpart JJJJJJ is satisfied by compliance with the more stringent six-year requirement.

#### Generators DAB-3, IAB-3, 99-1, TF-1, BLDG 600-1, and IAB-4

- Although 40 C.F.R. Part 60, Subpart IIII limits non-emergency engine use to 100-hours per year with unlimited use during emergency situations, Generator IAB-4 shall be limited to 500 hours per year of operation on a 12-month rolling total basis, including operating hours during emergency situations.

If there are periods of extended outage such as a natural disaster or other similar event outside BGR’s control, BGR may apply to the Department for a temporary variance to exempt specific time periods from this annual hour limit. The Department Commissioner may, without hearing, issue that variance for a period of time not to exceed 30 days if, in his/her judgement, the variance is necessary to avoid immediate threat to public health, safety, or general welfare or to protect critical infrastructure.

[06-096 C.M.R. ch. 169, § 4(B)(2)(c)]

- The fuel sulfur content for Generators DAB-3, IAB-3, 99-1, TF-1, BLDG 600-1, and IAB-4 shall be limited to 0.0015% sulfur by weight. Compliance shall be demonstrated by fuel delivery receipts from the supplier, fuel supplier certification, certificate of analysis, or testing of the fuel in the tank on-site. [06-096 C.M.R. ch. 115, BPT]

- Emissions shall not exceed the following:

| Unit | Pollutant | lb/MMBtu | Origin and Authority |
| --- | --- | --- | --- |
| Generator DAB-3 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |
| Generator IAB-3 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |
| Generator 99-1 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |
| Generator IAB-4 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT/BACT]:

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator IAB-3 | 0.71 | 0.71 | 0.71 | 0.01 | 18.88 | 5.02 | 0.53 |
| Generator DAB-3 | 0.56 | 0.56 | 0.56 | 0.01 | 15.04 | 4.00 | 0.42 |
| Generator 99-1 | 0.45 | 0.45 | 0.45 | 0.01 | 16.54 | 3.56 | 1.35 |
| Generator TF-1 | 0.20 | 0.20 | 0.20 | - | 7.41 | 1.6 | 0.60 |
| Generator BLDG 600-1 | 0.17 | 0.17 | 0.17 | - | 6.17 | 1.33 | 0.50 |
| Generator IAB-4 | 2.55 | 2.55 | 2.55 | 0.03 | 67.97 | 18.05 | 1.91 |

- Generator IAB-4 shall exhaust through a stack with a minimum height of 15 feet above ground level. [06-096 C.M.R. ch. 169, § 6(B)]

- Visible Emissions

- Visible emissions from Generators TF-1 and BLDG 600-1 shall each not exceed 20% opacity on a six-minute block average basis except for periods of startup during which time BGR shall either meet the normal operating visible emissions standard or the following work practice standards and alternative visible emissions standard.

- The duration of the startup shall not exceed 30 minutes per event;

- Visible emissions shall not exceed 50% opacity on a six-minute block average basis; and

- BGR shall keep records of the date, time, and duration of each startup.

Use of the work practice standards and alternative visible emissions standard in lieu of the normal operating standard is limited to no more than once per day.

Note: This does not limit the engine to one startup per day. It only limits the use of the alternative emission standard to once per day.

[06-096 C.M.R. ch. 101, § 4(A)(4)]

- Visible emissions from Generators DAB-3, IAB-3, 99-1, and IAB-4 shall each not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(4)]

- Generators TF-1 and BLDG 600-1 shall meet the applicable requirements of 40 C.F.R. Part 63, Subpart ZZZZ, including the following: [incorporated under 06-096 C.M.R. ch. 115, BPT]

- BGR shall meet the following operational limitations for each of the compression ignition emergency engines:

  - Change the oil and filter every 500 hours of operation or within 1 year + 30 days of the previous change, whichever comes first;

  - Inspect the air cleaner every 1,000 hours of operation or within 1 year + 30 days of the previous inspection, whichever comes first, and replace as necessary; and

  - Inspect the hoses and belts every 500 hours of operation or within 1 year + 30 days of the previous inspection, whichever comes first, and replace as necessary.

Records shall be maintained documenting compliance with the operational limitations.

[40 C.F.R. § 63.6603(a) and Table 2(d); and 06-096 C.M.R. ch. 115]

- Oil Analysis Program Option

BGR has the option of utilizing an oil analysis program which complies with the requirements of § 63.6625(i) in order to extend the specified oil change requirement. If this option is used, BGR must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for each engine. The analysis program must be part of the maintenance plan for each engine. [40 C.F.R. § 63.6625(i)]

- Non-Resettable Hour Meter

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 63.6625(f)]

- Maintenance, Testing, and Non-Emergency Operating Situations

- As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise to supply power as part of a financial arrangement with another entity). These limits are based on a calendar year. Compliance shall be demonstrated by records (electronic or written logs) of all engine operating hours. [40 C.F.R. § 63.6640(f) and 06-096 C.M.R. ch. 115]

- BGR shall keep records that include maintenance conducted on the engines and the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time. [40 C.F.R. §§ 63.6655(e) and (f)]

- Operation and Maintenance

The engines shall be operated and maintained according to the manufacturer’s emission-related written instructions, or BGR shall develop a maintenance plan which provides to the extent practicable for the maintenance and operation of each engine in a manner consistent with good air pollution control practice for minimizing emissions. [40 C.F.R. § 63.6625(e)]

BGR shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

- Startup Idle and Startup Time Minimization

During periods of startup, the facility must minimize each engine’s time spent at idle and minimize each engine’s startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes. [40 C.F.R. § 63.6625(h) & 40 C.F.R. Part 63, Subpart ZZZZ Table 2d]

- Generators DAB-3, IAB-3, 99-1, and IAB-4 shall meet the applicable requirements of 40 C.F.R. Part 60, Subpart IIII, including the following: [incorporated under 06-096 C.M.R. chs. 115 and 169, BPT/BACT]

- Manufacturer Certification

The engines shall be certified by the manufacturer as meeting the emission standards for new nonroad compression ignition engines found in § 60.4202. [40 C.F.R. § 60.4205(b)]

- Ultra-Low Sulfur Fuel

The fuel fired in the engines shall not exceed 15 ppm sulfur (0.0015% sulfur). Compliance with the fuel sulfur content limit shall be demonstrated by fuel delivery receipts from the supplier, fuel supplier certification, certificate of analysis, or testing of the fuel in the tank on-site. [40 C.F.R. § 60.4207(b) and 06-096 C.M.R. ch. 115, BPT]

- Non-Resettable Hour Meter

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4209(a)]

- Annual Time Limit for Maintenance and Testing

- As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). These limits are based on a calendar year. Compliance shall be demonstrated by records (electronic or written log) of all engine operating hours. [40 C.F.R. § 60.4211(f) and 06-096 C.M.R. ch. 115, BPT]

- BGR shall keep records that include the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time. BGR shall maintain records of engine operating times on a 12-month rolling total basis. The 12-month rolling total encompassing January through December of each calendar year shall be used to demonstrate compliance with the annual time limit for maintenance and testing pursuant to 40 C.F.R. § 60.4211(f) as described above. [40 C.F.R. § 60.4214(b),06-096 C.M.R. ch. 169, § 4(B)(2)(c), and 06-096 C.M.R. ch. 115]

- Operation and Maintenance

The engines shall be operated and maintained according to the manufacturer’s emission-related written instructions. BGR may only change those emission-related settings that are permitted by the manufacturer. [40 C.F.R. § 60.4211(a)]

BGR shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

#### Snow Melter #1

- Snow Melter #1 shall fire distillate fuel with a maximum fuel sulfur content of 0.0015% by weight. Records from the supplier documenting type of fuel delivered shall be kept for compliance purposes. [06-096 C.M.R. ch. 115, BPT]

- Snow Melter #1 shall not operate for more than 200 hours per calendar year. BGR shall record Snow Melter #1 operation time in a log to demonstrate compliance. [06-096 C.M.R. ch. 115, BPT]

- Emissions shall not exceed the following:

| Unit | Pollutant | lb/MMBtu | Origin and Authority |
| --- | --- | --- | --- |
| Snow Melter #1 | PM | 0.12 | 06-096 C.M.R. ch. 103, § (2)(B)(1)(a) |

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT]:

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Snow Melter #1 | 1.08 | 1.08 | 1.08 | 0.01 | 1.28 | 0.32 | 0.02 |

- Visible emissions from Snow Melter #1 shall not exceed 10% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 115, BPT]

#### Volatile Organic Liquid Storage Tanks

- Storage Tanks T-1, T-2, and T-3 shall be used to store only Jet A fuel or other volatile organic liquid with a true vapor pressure of less than 3.5 kPA. [06-096 C.M.R. ch. 115, BPT]

- Tank T-4 shall only contain Low Lead Aviation Gasoline. [06-096 C.M.R. ch. 115, BPT]

- Tank T-5 shall only contain Gasoline. [06-096 C.M.R. ch. 115, BPT]

- BGR shall keep records of total throughput for each tank on a calendar year basis. [06-096 C.M.R. ch. 115, BPT]

- BGR shall keep records showing the dimensions of Tanks T-4 and T-5 and analyses showing the capacities of the storage vessels. These records shall be kept for the life of the tanks and be readily available upon request. [06-096 C.M.R. ch. 115, BPT]

- BGR shall maintain fill pipes for Tanks T-4 and T-5 which extend to within six inches of the bottom of each tank. [06-096 C.M.R. ch. 118, § 4(A) for Tank T-5; 06-096 C.M.R. ch. 115, BPT for Tank T-4]

- BGR shall maintain gasoline throughput records that will allow the monthly and annual throughput of Tanks T-4 and T-5 to be determined. [06-096 C.M.R. ch 118, § 10(B) for Tank T-5; 06-096 C.M.R. ch. 115, BPT for Tank T-4]

#### General Process Sources

Visible emissions from any general process source shall not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(B)(4)]

#### Fugitive Emissions [06-096 C.M.R. ch. 101, § 4(C)]

- BGR shall not cause emissions of any fugitive dust during any period of construction, reconstruction, or operation without taking reasonable precautions. Such reasonable precautions shall be included in the facility’s continuing program of best management practices for suppression of fugitive particulate matter. See 06-096 C.M.R. ch. 101, § 4(C) for a list of potential reasonable precautions.

- BGR shall not cause or allow visible emissions within 20 feet of ground level, measured as any level of opacity and not including water vapor, beyond the legal boundary of the property on which such emissions occur. Compliance with this standard shall be determined pursuant to 40 C.F.R. Part 60, Appendix A, Method 22.

#### Additional Information

If the Department determines that any parameter value pertaining to construction and operation of the emissions units, including but not limited to stack size, configuration, flow rate, emission rates, nearby structures, etc., deviates from what was submitted in the application or ambient air quality impact analysis for this air emission license, BGR may be required to submit additional information. Upon written request from the Department, BGR shall provide information necessary to demonstrate AAQS will not be exceeded, potentially including submission of an ambient air quality impact analysis or an application to amend this air emission license to resolve any deficiencies and ensure compliance with AAQS. Submission of this information is due within 60 days of the Department’s written request unless otherwise stated in the Department’s letter.

[06-096 C.M.R. ch. 115, § 2(O)]

DONE AND DATED IN AUGUSTA, MAINE THIS 17th DAY OF MARCH, 2026.

DEPARTMENT OF ENVIRONMENTAL PROTECTION

BY:							for

MELANIE LOYZIM, COMMISSIONER

The term of this license shall be ten (10) years from the signature date above.

[Note: If a renewal application, determined as complete by the Department, is submitted prior to expiration of this license, then pursuant to Title 5 M.R.S. § 10002, all terms and conditions of the license shall remain in effect until the Department takes final action on the license renewal application.]

PLEASE NOTE ATTACHED SHEET FOR GUIDANCE ON APPEAL PROCEDURES

Date of initial receipt of application:		October 3, 2025

Date of application acceptance:		October 3, 2025

This Order prepared by Zac Hicks, Bureau of Air Quality.