# FINDINGS OF FACT

After review of the air emission license amendment application, staff investigation reports, and other documents in the applicant’s file in the Bureau of Air Quality, pursuant to 38 Maine Revised Statutes (M.R.S.) § 344 and § 590, the Maine Department of Environmental Protection (Department) finds the following facts:

## REGISTRATION

### Introduction

Regional School Unit #14 – Raymond Campus (Raymond) was issued Air Emission License A-1052-71-B-R on November 21, 2016, for the operation of emission sources associated with their educational facility. The license was subsequently amended as follows:

| Amendment # | Date Issued | Brief Description |
| --- | --- | --- |
| A-1052-71-C-A | October 25, 2019 | Replacing Boiler #1 with two new units, #1A and #1B |
| A-1052-71-D-M | November 9, 2022 | Adding propane as a fuel for Boiler #2 |
| A-1052-71-E-A | November 19, 2024 | Replacing Boiler #2 with two new smaller units, #2A and #2B |

The equipment addressed in this license amendment is located at 434 Webb Mills Rd, Raymond, Maine.

Raymond has requested an amendment to their license to remove Generator #2, which will be replaced with three new propane-fired generators that will be located at the Raymond Elementary School.

### Emission Equipment

The following equipment is addressed in this air emission license amendment:

Stationary Engines

| ### Equipment | Max. Input Capacity (MMBtu/hr) | Rated Output Capacity (kW) | Fuel Type | Firing Rate | Date of Manuf. | ### Date of Install. |
| --- | --- | --- | --- | --- | --- | --- |
| Generator #2* | 0.58 | 50 | Distillate Fuel | 4.2 gal/hr | 1990 | 1990 |
| RES Generator #3** | 1.56 | 132.6 | Propane | 622 scf/hr | 2026 | Expected July 2026 |
| RES Generator #4** | 1.56 | 132.6 | Propane | 622 scf/hr | 2026 | Expected July 2026 |
| RES Generator #5** | 1.56 | 132.6 | Propane | 622 scf/hr | 2026 | Expected July 2026 |

* Removed from license

** New to the license

### Definitions

Distillate Fuel means the following:

- Fuel oil that complies with the specifications for fuel oil numbers 1 or 2, as defined by the American Society for Testing and Materials (ASTM) in ASTM D396;

- Diesel fuel oil numbers 1 or 2, as defined in ASTM D975;

- Kerosene, as defined in ASTM D3699;

- Biodiesel, as defined in ASTM D6751; or

- Biodiesel blends, as defined in ASTM D7467.

Records or Logs mean either hardcopy or electronic records.

### Application Classification

All rules, regulations, or statutes referenced in this air emission license refer to the amended version in effect as of the date this license was issued.

The modification of a minor source is considered a major or minor modification based on whether or not expected emission increases exceed the “Significant Emissions” levels as defined in the Department’s Definitions Regulation, 06-096 Code of Maine Rules (C.M.R.) ch. 100. The emission increases are determined by subtracting the current licensed annual emissions preceding the modification from the maximum future licensed annual emissions, as follows:

| Pollutant | Current License (tpy) | Future License (tpy) | Net Change (tpy) | Significant Emissions Levels |
| --- | --- | --- | --- | --- |
| PM | 2.2 | 2.1 | - 0.1 | 100 |
| PM10 | 2.2 | 2.1 | - 0.1 | 100 |
| PM2.5 | 2.2 | 2.1 | - 0.1 | 100 |
| SO2 | 0.2 | 0.1 | - 0.1 | 100 |
| NOx | 5.0 | 5.8 | + 0.8 | 100 |
| CO | 2.8 | 2.8 | -- | 100 |
| VOC | 0.5 | 0.4 | - 0.1 | 100 |

This modification is determined to be a minor modification and has been processed as such.

### Facility Classification

With the annual operating hours restriction on the emergency generators, the facility is licensed as follows:

- As a synthetic minor source of air emissions for criteria pollutants, because Raymond is subject to license restrictions that keep facility emissions below major source thresholds for NOx; and

- As an area source of hazardous air pollutants (HAP), because the licensed emissions are below the major source thresholds for HAP.

## BEST PRACTICAL TREATMENT (BPT)

### Introduction

In order to receive a license, the applicant must control emissions from each unit to a level considered by the Department to represent Best Practical Treatment (BPT), as defined in Definitions Regulation, 06-096 C.M.R. ch. 100. Separate control requirement categories exist for new and existing equipment.

BPT for new sources and modifications requires a demonstration that emissions are receiving Best Available Control Technology (BACT), as defined in Definitions Regulation, 06-096 C.M.R. ch. 100. BACT is a top-down approach to selecting air emission controls considering economic, environmental, and energy impacts.

### RES Generators #3, #4, and #5

Raymond has proposed the installation of three new emergency generators. The emergency generators are generator sets with each gen set consisting of an engine and an electrical generator. The emergency generators have engines rated at 1.56 MMBtu/hr, each, and all three fire propane. The new emergency generators were all manufactured in 2025.

##### BACT Findings

The BACT emission limits for RES Generators #3, #4, and #5 are based on the following:

| PM/PM10/PM2.5 | – | 0.05 lb/MMBtu, 06-096 C.M.R. ch. 115, BACT |
| --- | --- | --- |
| SO2 | – | 5.88 x 10-4 lb/MMBtu from AP-42 Table 3.2-3 dated 10/24 |
| NOx | – | 4.08 lb/MMBtu from AP-42 Table 3.2-3 dated 10/24 |
| CO | – | 0.317 lb/MMBtu from AP-42 Table 3.2-3 dated 10/24 |
| VOC | – | 0.118 lb/MMBtu from AP-42 Table 3.2-3 dated 10/24 |
| Visible Emissions | – | 06-096 C.M.R. ch. 115, BACT |

The BACT emission limits for RES Generators #3, #4, and #5 are the following:

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RES Generator #3 | 0.08 | 0.08 | 0.08 | -- | 6.36 | 0.49 | 0.18 |
| RES Generator #4 | 0.08 | 0.08 | 0.08 | -- | 6.36 | 0.49 | 0.18 |
| RES Generator #5 | 0.08 | 0.08 | 0.08 | -- | 6.36 | 0.49 | 0.18 |

Visible emissions from RES Generators #3, #4, and #5 shall each not exceed 10% opacity on a six-minute block average basis.

The Department has determined that the BACT visible emission limit is more stringent than the applicable limit in 06-096 C.M.R. ch. 101. Therefore, the visible emission limit for each generator has been streamlined to the more stringent BACT limit, and only this more stringent limit shall be included in the Order of this air emission license.

##### Chapter 169

Stationary Generators, 06-096 C.M.R. ch. 169 (Chapter 169), is applicable to RES Generators #3, #4, and #5. They are emergency generators powered by engines with rated outputs of less than 1,000 brake horsepower (747 kW). Chapter 169 identifies emission standards for generator engines subject to this chapter and stack height requirements for certain generator engines subject to this chapter.

- Chapter 169 Emission Standards Requirements

For RES Generators #3, #4, and #5, Raymond shall comply with the emission standards for emergency generators by complying with the applicable standards contained in 40 C.F.R. Part 60, Subpart JJJJ. [06-096 C.M.R. ch. 169, § 4(B)(1)]

- Chapter 169 Stack Height Requirements

Chapter 169 identifies stack height requirements for any stack used to exhaust a generator engine or combination of generator engines with a combined rated output equal to or greater than 1,000 brake horsepower (747 kW). Individual generator engines with a maximum power capacity of less than 300 kW are not included in the assessment of the combined generator power capacity exhausted through a common stack. [06-096 C.M.R. ch. 169, § 6]

There are no stack height requirements in Chapter 169 applicable to RES Generators #3, #4, and #5 because each unit exhausts through its own stack and has a rated output less than 1,000 brake horsepower (747 kilowatts). [06-096 C.M.R. ch. 169, § 6]

##### New Source Performance Standards

Standards of Performance for Spark Ignition Internal Combustion Engines, 40 C.F.R. Part 60, Subpart JJJJ is applicable to the emergency engines listed above since the units were ordered after June 12, 2006, and manufactured after January 1, 2009. [40 C.F.R. § 60.4230]

A summary of applicable federal 40 C.F.R. Part 60, Subpart JJJJ requirements is listed below.

- Emergency Engine Designation and Operating Criteria

Under 40 C.F.R. Part 60, Subpart JJJJ, a stationary reciprocating internal combustion engine (ICE) is considered an emergency stationary ICE (emergency engine) as long as the engine is operated in accordance with the following criteria.  Operation of an engine outside of the criteria specified below may cause the engine to no longer be considered an emergency engine under 40 C.F.R. Part 60, Subpart JJJJ, resulting in the engine being subject to requirements of this subpart applicable to non-emergency engines.

- Emergency Situation Operation (On-Site)

There is no operating time limit on the use of an emergency engine to provide electrical power or mechanical work during an emergency situation. Examples of use of an emergency engine during emergency situations include the following:

- Use of an engine to produce power for critical networks or equipment (including power supplied to portions of a facility) because of failure or interruption of electric power from the local utility (or the normal power source, if the facility runs on its own power production);

- Use of an engine to mitigate an on-site disaster;

- Use of an engine to pump water in the case of fire, flood, natural disaster, or severe weather conditions; and

- Similar instances.

- Non-Emergency Situation Operation

An emergency engine may be operated up to a maximum of 100 hours per calendar year for maintenance checks, readiness testing, and other non-emergency situations as described below.

- An emergency engine may be operated for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government; the manufacturer; the vendor; the regional transmission organization or equivalent balancing authority and transmission operator; or the insurance company associated with the engine. The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency ICE more than 100 hours per calendar year.

- An emergency engine may be operated for up to 50 hours per calendar year for other non-emergency situations.  However, these operating hours are counted as part of the 100 hours per calendar year operating limit described in paragraph (2) and (2) (i) above.

The 50 hours per calendar year operating limit for other non-emergency situations cannot be used for peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 C.F.R. §§ 60.4243(d) and 60.4248]

- 40 C.F.R. Part 60, Subpart JJJJ Requirements

- Manufacturer Certification Requirement

The engines shall be certified by the manufacturer as meeting the emission standards for new nonroad spark ignition engines found in 40 C.F.R. Part 60, Subpart JJJJ, Table 1. [40 C.F.R. § 60.4233]

- Non-Resettable Hour Meter Requirement

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4237]

- Operation and Maintenance Requirement

The engines shall be operated and maintained according to the manufacturer’s written instructions or procedures developed by Raymond that are approved by the engine manufacturer. Raymond may only change those settings that are permitted by the manufacturer. [40 C.F.R. § 60.4243]

Raymond shall have available for review by the Department a copy of the manufacturer’s written instructions or procedures developed by Raymond that are approved by the engine manufacturer for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

- Annual Time Limit for Maintenance and Testing

As emergency engines, the units shall each be limited to 100 hours/year for maintenance and testing. The emergency engines may operate up to 50 hours per year in non-emergency situations, but those 50 hours are included in the 100 hours total allowed for maintenance and testing. The 50 hours for non-emergency use cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity. [40 C.F.R. § 60.4243(d)]

- Recordkeeping

Raymond shall keep records that include maintenance conducted on the engines and the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time. [40 C.F.R. § 60.4245(b)]

- National Emission Standards for Hazardous Air Pollutants (NESHAP): 40 C.F.R. Part 63, Subpart ZZZZ

Pursuant to 40 C.F.R. § 63.6590(c), stationary spark ignition engines subject to regulations under 40 C.F.R. Part 60, Subpart JJJJ must meet the requirements of Subpart ZZZZ by meeting the requirements of 40 C.F.R. Part 60, Subpart JJJJ. No further requirements apply for such engines under Subpart ZZZZ. [40 C.F.R. § 63.6590(c)]

### Annual Emissions

The table below provides an estimate of facility-wide annual emissions for the purposes of calculating the facility’s annual air license fee and establishing the facility’s potential to emit (PTE). Only licensed equipment is included, i.e., emissions from insignificant activities are excluded. Similarly, unquantifiable fugitive particulate matter emissions are not included except when required by state or federal regulations. Maximum potential emissions were calculated based on the following assumptions:

- Operating the boilers for 8,760 hr/yr each; and

- Operating JSMS Generator #1 and RES Generators #3, #4, and #5 for 100 hrs/yr of non-emergency operation.

This information does not represent a comprehensive list of license restrictions or permissions. That information is provided in the Order section of this license.

Total Licensed Annual Emissions for the Facility

Tons/year

(used to calculate the annual license fee)

|  | PM | PM10 | PM2.5 | SO2 | NOx | CO | VOC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Boilers | 2.1 | 2.1 | 2.1 | 0.1 | 4.6 | 2.7 | 0.4 |
| JSMS Generator #1 | -- | -- | -- | -- | 0.2 | -- | -- |
| RES Generators #3, #4, #5 | -- | -- | -- | -- | 1.0 | 0.1 | -- |
| Total TPY | 2.1 | 2.1 | 2.1 | 0.1 | 5.8 | 2.8 | 0.4 |

| Pollutant | Tons/year |
| --- | --- |
| Single HAP | 7.9 |
| Total HAP | 19.9 |

## AMBIENT AIR QUALITY ANALYSIS

The level of ambient air quality impact modeling required for a minor source is determined by the Department on a case-by-case basis. In accordance with 06-096 C.M.R. ch. 115, an ambient air quality impact analysis is not required for a minor source if the total licensed annual emissions of any pollutant released do not exceed the following levels and there are no extenuating circumstances:

| Pollutant | Tons/Year |
| --- | --- |
| PM10 | 25 |
| PM2.5 | 15 |
| SO2 | 50 |
| NOx | 50 |
| CO | 250 |

The total licensed annual emissions for the facility are below the emission levels contained in the table above and there are no extenuating circumstances; therefore, an ambient air quality impact analysis is not required as part of this license amendment.

This determination is based on information provided by the applicant regarding the expected construction and operation of the proposed Generators #3, #4, and #5, and the existing licensed emission units. If the Department determines that any parameter (e.g., stack size, configuration, flow rate, emission rates, nearby structures, etc.) deviates from what was included in the application, the Department may require Raymond to submit additional information and may require an ambient air quality impact analysis at that time.

# ORDER

Based on the above Findings and subject to conditions listed below, the Department concludes that the emissions from this source:

- will receive Best Practical Treatment,

- will not violate applicable emission standards, and

- will not violate applicable ambient air quality standards in conjunction with emissions from other sources.

The Department hereby grants Air Emission License Amendment A-1052-71-F-A subject to the conditions found in Air Emission License A-1052-71-B-R; in amendments A-1052-71-C-A, A-1052-71-D-M, and A-1052-71-E-A; and the following conditions.

Severability. The invalidity or unenforceability of any provision of this License Amendment or part thereof shall not affect the remainder of the provision or any other provisions. This License Amendment shall be construed and enforced in all respects as if such invalid or unenforceable provision or part thereof had been omitted.

## SPECIFIC CONDITIONS

The following shall replace Condition (17) of Air Emission License A-1052-71-B-R (11/21/2016) and Condition (17) F as amended in Air Emission License Amendment A-1052-71-E-A (11/19/2024):

#### JSMS Generator #1, and RES Generators #3, #4, and #5

- JSMS Generator #1 and RES Generators #3, #4, and #5 are licensed to fire propane. [06-096 C.M.R. ch. 115, BPT]

- Each of the emergency generators shall be limited to 100 hours of operation per calendar year, excluding operating hours during emergency situations. [06-096 C.M.R. ch. 115, BPT]

- Emissions shall not exceed the following [06-096 C.M.R. ch. 115, BPT]:

| ### Unit | PM (lb/hr) | PM10 (lb/hr) | PM2.5 (lb/hr) | SO2 (lb/hr) | NOx (lb/hr) | CO (lb/hr) | VOC (lb/hr) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| JSMS Generator #1 | 0.05 | 0.05 | 0.05 | -- | 4.00 | 0.31 | 0.12 |
| RES Generator #3 | 0.08 | 0.08 | 0.08 | -- | 6.36 | 0.49 | 0.18 |
| RES Generator #4 | 0.08 | 0.08 | 0.08 | -- | 6.36 | 0.49 | 0.18 |
| RES Generator #5 | 0.08 | 0.08 | 0.08 | -- | 6.36 | 0.49 | 0.18 |

- Visible Emissions

JSMS Generator #1

Visible emissions from JSMS Generator #1 shall not exceed 20% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 101, § 4(A)(4)]

RES Generators #3, #4, and #5

Visible emissions from RES Generators #3, #4, and #5 shall not exceed 10% opacity on a six-minute block average basis. [06-096 C.M.R. ch. 115, BACT]

- The Emergency Generators #1, #3, #4, and #5 shall meet the applicable requirements of 40 C.F.R. Part 60, Subpart JJJJ, including the following: [incorporated under 06-096 C.M.R. ch. 115, BPT]

- Manufacturer Certification

The engines shall be certified by the manufacturer as meeting the emission standards for new nonroad spark ignition engines found in 40 C.F.R. Part 60, Subpart JJJJ, Table 1.

- Non-Resettable Hour Meter

A non-resettable hour meter shall be installed and operated on each engine. [40 C.F.R. § 60.4237 and 06-096 C.M.R. ch. 115, BPT]

- Annual Time Limit for Maintenance and Testing

- As emergency engines, the units shall each be limited to 100 hours/year for maintenance checks and readiness testing. Up to 50 hours/year of the 100 hours/year may be used in non-emergency situations (this does not include peak shaving, demand response, or to generate income for a facility by providing power to an electric grid or otherwise supply power as part of a financial arrangement with another entity). The limits are based on a calendar year. Compliance shall be demonstrated by records (electronic or written log) of all engine operating hours. [40 C.F.R. § 60.4243(d) and 06-096 C.M.R. ch. 115, BPT]

- Raymond shall keep records that include maintenance conducted on the engines and the hours of operation of each engine recorded through the non-resettable hour meter. Documentation shall include the number of hours each unit operated for emergency purposes, the number of hours each unit operated for non-emergency purposes, and the reason each engine was in operation during each time. [40 C.F.R. § 60.4245(b)]

- Operation and Maintenance

Each engine shall be operated and maintained according to the manufacturer’s written instructions or procedures developed by Raymond that are approved by the engine manufacturer. Raymond may only change those settings that are permitted by the manufacturer. [40 C.F.R. § 60.4243]

Raymond shall have available for review by the Department a copy of the manufacturer’s emission-related written instructions for engine operation and maintenance. [06-096 C.M.R. ch. 115, BPT]

DONE AND DATED IN AUGUSTA, MAINE THIS 20th DAY OF 	MARCH, 2026.

DEPARTMENT OF ENVIRONMENTAL PROTECTION

BY:							for

MELANIE LOYZIM, COMMISSIONER

The term of this license amendment shall be concurrent with the term of Air Emission License A-1052-71-B-R (issued 11/21/2016).

[Note: If a renewal application, determined as complete by the Department, is submitted prior to expiration of this license, then pursuant to Title 5 M.R.S. § 10002, all terms and conditions of the license shall remain in effect until the Department takes final action on the license renewal application.]

PLEASE NOTE ATTACHED SHEET FOR GUIDANCE ON APPEAL PROCEDURES

Date of initial receipt of application:	1/13/2026

Date of application acceptance:	1/13/2026

This Order prepared by Jack Doran, Bureau of Air Quality.